## Preliminary Constraints >345 kV
Initial Constraints for Scenario 1, Block 1
Loading (%) | Estimated Loading (MVA) | Rate B (MVA) | TDF | Limiting Constraint | Contingency | PreShift | Rating
New England ISO
109.5618 | 1643.4264 | 1500 | -0.01483 | 119259 LONG MTN 345 119272 NE_398_NY 345 1 | C:104095 DEERFIELD 345 124009 FRANKLIN 345 1 | -424 | -1500
120.6416 | 1809.6246 | 1500 | -0.02143 | 119259 LONG MTN 345 119272 NE_398_NY 345 1 | C:116023 BERKSHIRE 345 116034 NE_393_NY 345 1 | -47.5 | -1500
120.6483 | 1809.7246 | 1500 | -0.02143 | 119259 LONG MTN 345 119272 NE_398_NY 345 1 | C:116034 NE_393_NY 345 137450 ALPS345 345 1 | -47.6 | -1500
118.5805 | 1643.5264 | 1386 | -0.01483 | 119272 NE_398_NY 345 126294 PLTVLLEY 345 1 | C:104095 DEERFIELD 345 124009 FRANKLIN 345 1 | -424.1 | -1386
130.5718 | 1809.7246 | 1386 | -0.02143 | 119272 NE_398_NY 345 126294 PLTVLLEY 345 1 | C:116023 BERKSHIRE 345 116034 NE_393_NY 345 1 | -47.6 | -1386
130.579 | 1809.8246 | 1386 | -0.02143 | 119272 NE_398_NY 345 126294 PLTVLLEY 345 1 | C:116034 NE_393_NY 345 137450 ALPS345 345 1 | -47.7 | -1386
New York ISO
111.7001 | 1481.1433 | 1326 | -0.01605 | 137450 ALPS345 345 137452 N.SCOT77 345 1 | C:119259 LONG MTN 345 119272 NE_398_NY 345 1 | -161.4 | -1326
111.7076 | 1481.2433 | 1326 | -0.01605 | 137450 ALPS345 345 137452 N.SCOT77 345 1 | C:119272 NE_398_NY 345 126294 PLTVLLEY 345 1 | -161.5 | -1326
IESO
146.0859 | 2872.048 | 1966 | 0.01237 | 152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | C:153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | 1854.9 | 1966
146.0859 | 2872.048 | 1966 | 0.01237 | 152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | C:152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | 1854.9 | 1966
146.859 | 2887.248 | 1966 | 0.01237 | 152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | C:152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | 1870.1 | 1966
159.5276 | 2873.5703 | 1801.3 | 0.01238 | 152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | C:153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | 1855.6 | 1801.3
159.5276 | 2873.5703 | 1801.3 | 0.01238 | 152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | C:152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | 1855.6 | 1801.3
160.377 | 2888.8703 | 1801.3 | 0.01238 | 152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | C:152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | 1870.9 | 1801.3
104.9646 | 2855.248 | 2720.2 | 0.01237 | 152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | C:153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | 1838.1 | 2720.2
104.9646 | 2855.248 | 2720.2 | 0.01237 | 152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | C:152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | 1838.1 | 2720.2
105.5234 | 2870.448 | 2720.2 | 0.01237 | 152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | C:152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | 1853.3 | 2720.2
105.0243 | 2856.8703 | 2720.2 | 0.01238 | 152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | C:153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | 1838.9 | 2720.2
105.0243 | 2856.8703 | 2720.2 | 0.01238 | 152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | C:152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | 1838.9 | 2720.2
105.5831 | 2872.0703 | 2720.2 | 0.01238 | 152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | C:152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | 1854.1 | 2720.2
145.2387 | 2855.248 | 1965.9 | -0.01237 | 153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | C:152011 NOBEL_X504EN 500 153011 NOBEL_X504ES 500 1 | -1838.1 | -1965.9
145.2387 | 2855.248 | 1965.9 | -0.01237 | 153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | C:153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | -1838.1 | -1965.9
146.0119 | 2870.448 | 1965.9 | -0.01237 | 153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | C:152000 HANMER_TS 500 152011 NOBEL_X504EN 500 1 | -1853.3 | -1965.9
151.3173 | 2856.8703 | 1888 | -0.01238 | 153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | C:153000 ESSA_TS 500 153010 NOBEL_X503ES 500 1 | -1838.9 | -1888
151.3173 | 2856.8703 | 1888 | -0.01238 | 153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | C:152010 NOBEL_X503EN 500 153010 NOBEL_X503ES 500 1 | -1838.9 | -1888
152.1224 | 2872.0703 | 1888 | -0.01238 | 153000 ESSA_TS 500 153011 NOBEL_X504ES 500 1 | C:152000 HANMER_TS 500 152010 NOBEL_X503EN 500 1 | -1854.1 | -1888
HQ
177.1632 | 1248.8236 | 704.9 | -0.01191 | 180304 LTD315 315 180317 JCA315 315 1 | Base Case | 269.5 | -704.9
218.8031 | 1542.3433 | 704.9 | -0.01605 | 180304 LTD315 315 180317 JCA315 315 1 | C:180304 LTD315 315 180704 LTD735 735 2 | 222.6 | -704.9
229.9273 | 1620.7577 | 704.9 | -0.01673 | 180304 LTD315 315 180317 JCA315 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | 245.1 | -704.9
244.1663 | 1721.128 | 704.9 | -0.01748 | 180304 LTD315 315 180317 JCA315 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 283.8 | -704.9
259.2616 | 933.8604 | 360.2 | 0.01031 | 180304 LTD315 315 180550 DBOPR1 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -86.1 | 360.2
266.6989 | 960.6495 | 360.2 | 0.01035 | 180304 LTD315 315 180551 DBOPR2 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -109.6 | 360.2
136.8013 | 1852.5636 | 1354.2 | -0.02028 | 180304 LTD315 315 180704 LTD735 735 1 | C:180433 B1-315 315 180434 B2-315 315 1 | -185 | -1354.2
136.9013 | 1853.9169 | 1354.2 | -0.01981 | 180304 LTD315 315 180704 LTD735 735 1 | C:180304 LTD315 315 180704 LTD735 735 2 | -225 | -1354.2
139.2878 | 1886.2355 | 1354.2 | -0.02139 | 180304 LTD315 315 180704 LTD735 735 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -127.4 | -1354.2
137.1056 | 1856.6837 | 1354.2 | -0.01984 | 180304 LTD315 315 180704 LTD735 735 2 | C:180304 LTD315 315 180704 LTD735 735 1 | -225.3 | -1354.2
137.2026 | 1857.9972 | 1354.2 | -0.02034 | 180304 LTD315 315 180704 LTD735 735 2 | C:180433 B1-315 315 180434 B2-315 315 1 | -185.5 | -1354.2
139.6817 | 1891.5692 | 1354.2 | -0.02145 | 180304 LTD315 315 180704 LTD735 735 2 | C:180434 B2-315 315 180642 D_HTV 315 1 | -127.8 | -1354.2
283.9738 | 1017.194 | 358.2 | 0.01037 | 180304 LTD315 315 183501 SGBPR31-315D 315 1 | C:180433 B1-315 315 183561 SGBPR21-315D 315 2 | -164.5 | 358.2
316.5368 | 1133.8349 | 358.2 | 0.01196 | 180304 LTD315 315 183501 SGBPR31-315D 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -150.4 | 358.2
419.4843 | 1502.5926 | 358.2 | 0.01706 | 180304 LTD315 315 183501 SGBPR31-315D 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | -99.8 | 358.2
271.6127 | 972.9167 | 358.2 | 0.01047 | 180304 LTD315 315 183561 SGBPR21-315D 315 2 | C:180433 B1-315 315 180434 B2-315 315 1 | -112 | 358.2
289.6194 | 1037.4167 | 358.2 | 0.01047 | 180304 LTD315 315 183586 SGBPR22-315D 315 2 | C:180433 B1-315 315 180434 B2-315 315 1 | -176.5 | 358.2
292.9153 | 1049.2227 | 358.2 | 0.01173 | 180304 LTD315 315 183613 DBOPO1 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -84.7 | 358.2
296.579 | 1062.3458 | 358.2 | 0.01192 | 180304 LTD315 315 183613 DBOPO1 315 1 | C:180304 LTD315 315 183614 DBOPO2 315 1 | -82.2 | 358.2
395.689 | 1417.3581 | 358.2 | 0.01682 | 180304 LTD315 315 183613 DBOPO1 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | -34.3 | 358.2
271.1612 | 971.2996 | 358.2 | 0.01154 | 180304 LTD315 315 183614 DBOPO2 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -22.4 | 358.2
283.8361 | 1016.7009 | 358.2 | 0.01181 | 180304 LTD315 315 183614 DBOPO2 315 1 | C:180304 LTD315 315 183613 DBOPO1 315 1 | -45.6 | 358.2
389.7982 | 1396.2573 | 358.2 | 0.01664 | 180304 LTD315 315 183614 DBOPO2 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | 28 | 358.2
249.3102 | 898.0154 | 360.2 | 0.0102 | 180305 MAN315 315 180642 D_HTV 315 1 | C:180305 MAN315 315 180643 HTV315 315 2 | 59.3 | 360.2
253.0398 | 911.4494 | 360.2 | 0.01035 | 180305 MAN315 315 180642 D_HTV 315 1 | C:180305 MAN315 315 180643 HTV315 315 1 | 60.4 | 360.2
528.1192 | 1902.2852 | 360.2 | 0.02249 | 180305 MAN315 315 180642 D_HTV 315 1 | C:180642 D_HTV 315 180643 HTV315 315 1 | -53 | 360.2
109.9733 | 897.3818 | 816 | 0.01014 | 180305 MAN315 315 180643 HTV315 315 1 | C:180305 MAN315 315 180643 HTV315 315 2 | 63.6 | 816
111.6645 | 911.1826 | 816 | 0.01032 | 180305 MAN315 315 180643 HTV315 315 1 | C:180305 MAN315 315 180642 D_HTV 315 1 | 62.6 | 816
854.6214 | 3078.3463 | 360.2 | -0.03527 | 180433 B1-315 315 180434 B2-315 315 1 | Base Case | -178.2 | -360.2
870.7202 | 3136.3341 | 360.2 | -0.03504 | 180433 B1-315 315 180434 B2-315 315 1 | C:180437 QE315B 315 183667 DFRT1A 315 1 | -255.1 | -360.2
904.0939 | 3256.5463 | 360.2 | -0.03527 | 180433 B1-315 315 180434 B2-315 315 1 | C:180319 CHA315 315 180519 CHAT G2 315 1 | -356.4 | -360.2
904.0939 | 3256.5463 | 360.2 | -0.03527 | 180433 B1-315 315 180434 B2-315 315 1 | C:180319 CHA315 315 180419 CHAT G 315 1 | -356.4 | -360.2
284.9509 | 1020.694 | 358.2 | -0.01037 | 180433 B1-315 315 183501 SGBPR31-315D 315 1 | C:180433 B1-315 315 183561 SGBPR21-315D 315 2 | 168 | -358.2
317.5139 | 1137.3349 | 358.2 | -0.01196 | 180433 B1-315 315 183501 SGBPR31-315D 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 153.9 | -358.2
420.4614 | 1506.0926 | 358.2 | -0.01706 | 180433 B1-315 315 183501 SGBPR31-315D 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | 103.3 | -358.2
270.2636 | 968.0844 | 358.2 | -0.01068 | 180433 B1-315 315 183561 SGBPR21-315D 315 2 | C:180319 CHA315 315 180419 CHAT G 315 1 | 89.9 | -358.2
285.4507 | 1022.4844 | 358.2 | -0.01068 | 180433 B1-315 315 183561 SGBPR21-315D 315 2 | Base Case | 144.3 | -358.2
379.9191 | 1360.8701 | 358.2 | -0.01467 | 180433 B1-315 315 183561 SGBPR21-315D 315 2 | C:180434 B2-315 315 180642 D_HTV 315 1 | 154.6 | -358.2
506.5141 | 1814.3334 | 358.2 | -0.02094 | 180433 B1-315 315 183561 SGBPR21-315D 315 2 | C:180433 B1-315 315 180434 B2-315 315 1 | 92.5 | -358.2
283.7876 | 1016.5272 | 358.2 | -0.01034 | 180433 B1-315 315 183613 DBOPO1 315 1 | C:180433 B1-315 315 183561 SGBPR21-315D 315 2 | 166.3 | -358.2
316.1211 | 1132.3458 | 358.2 | -0.01192 | 180433 B1-315 315 183613 DBOPO1 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 152.2 | -358.2
418.8948 | 1500.4813 | 358.2 | -0.01701 | 180433 B1-315 315 183613 DBOPO1 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | 101.8 | -358.2
284.2963 | 1018.3494 | 358.2 | -0.01035 | 180433 B1-315 315 183614 DBOPO2 315 1 | C:180433 B1-315 315 183561 SGBPR21-315D 315 2 | 167.3 | -358.2
316.6298 | 1134.1681 | 358.2 | -0.01193 | 180433 B1-315 315 183614 DBOPO2 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 153.2 | -358.2
419.4036 | 1502.3035 | 358.2 | -0.01702 | 180433 B1-315 315 183614 DBOPO2 315 1 | C:180433 B1-315 315 180434 B2-315 315 1 | 102.8 | -358.2
340.49 | 1116.8071 | 328 | -0.01078 | 180434 B2-315 315 180454 DCHVO2 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 230.4 | -328
305.7981 | 1101.4848 | 360.2 | -0.01077 | 180434 B2-315 315 180460 BASQUE 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 215.9 | -360.2
540.3175 | 1946.2236 | 360.2 | -0.02354 | 180434 B2-315 315 180642 D_HTV 315 1 | C:180706 MIC735 735 180718 SAG735 735 &1 | -10.6 | -360.2
559.1438 | 2014.0358 | 360.2 | -0.02377 | 180434 B2-315 315 180642 D_HTV 315 1 | C:180319 CHA315 315 180519 CHAT G2 315 1 | -59.5 | -360.2
559.1438 | 2014.0358 | 360.2 | -0.02377 | 180434 B2-315 315 180642 D_HTV 315 1 | C:180319 CHA315 315 180419 CHAT G 315 1 | -59.5 | -360.2
559.6157 | 2015.7358 | 360.2 | -0.02377 | 180434 B2-315 315 180642 D_HTV 315 1 | Base Case | 61.2 | -360.2
336.2588 | 1102.9289 | 328 | 0.0107 | 180453 DCHVO1 315 180460 BASQUE 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | -223.1 | 328
281.7 | 1014.6835 | 360.2 | -0.0105 | 180453 DCHVO1 315 180551 DBOPR2 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 151.3 | -360.2
271.9523 | 979.5721 | 360.2 | -0.01045 | 180454 DCHVO2 315 180550 DBOPR1 315 1 | C:180434 B2-315 315 180642 D_HTV 315 1 | 120.3 | -360.2
387.1677 | 1394.1909 | 360.1 | -0.0167 | 180642 D_HTV 315 180643 HTV315 315 1 | C:180319 CHA315 315 180519 CHAT G2 315 1 | 21 | -360.1
387.1677 | 1394.1909 | 360.1 | -0.0167 | 180642 D_HTV 315 180643 HTV315 315 1 | C:180319 CHA315 315 180419 CHAT G 315 1 | 21 | -360.1
409.2449 | 1473.6909 | 360.1 | -0.0167 | 180642 D_HTV 315 180643 HTV315 315 1 | Base Case | 100.5 | -360.1
553.4824 | 1993.09 | 360.1 | -0.02348 | 180642 D_HTV 315 180643 HTV315 315 1 | C:180305 MAN315 315 180642 D_HTV 315 1 | 62.4 | -360.1
254.1364 | 910.3167 | 358.2 | -0.01047 | 183561 SGBPR21-315D 315 183586 SGBPR22-315D 315 2 | C:180433 B1-315 315 180434 B2-315 315 1 | 49.4 | -358.2
PJM
101.8631 | 2133.0129 | 2094 | -0.01433 | 235102 01BELMNT 500 242920 05BELMON 765 1 | C:242920 05BELMON 765 242925 05KAMMER 765 1 | -954.7 | -2094
111.0196 | 2324.7511 | 2094 | -0.01767 | 235102 01BELMNT 500 242920 05BELMON 765 1 | C:235634 01WELTON SP 765 242508 05AMOS 765 1 | -871.8 | -2094
104.5416 | 3178.066 | 3040 | -0.01615 | 235632 01KEMPTOWN 500 235636 01KEMPTOWN 765 1 | C:235632 01KEMPTOWN 500 235636 01KEMPTOWN 765 2 | -1850.1 | -3040
104.5416 | 3178.066 | 3040 | -0.01615 | 235632 01KEMPTOWN 500 235636 01KEMPTOWN 765 2 | C:235632 01KEMPTOWN 500 235636 01KEMPTOWN 765 1 | -1850.1 | -3040
101.885 | 3097.3042 | 3040 | 0.01949 | 235634 01WELTON SP 765 235637 01WELTON SP 500 1 | C:235634 01WELTON SP 765 235636 01KEMPTOWN 765 1 | 1494.7 | 3040
103.4756 | 4400.8174 | 4253 | 0.02457 | 242516 05MOUNTN 765 242920 05BELMON 765 1 | C:235634 01WELTON SP 765 242508 05AMOS 765 1 | 2380.5 | 4253
116.3717 | 1814.2348 | 1559 | -0.01425 | 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1 | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | -642.5 | -1559
116.423 | 1815.0348 | 1559 | -0.01425 | 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1 | C:382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | -643.3 | -1559
138.7439 | 2163.0179 | 1559 | -0.0177 | 242521 05NAGEL 500 360102 8PHIPPS B NP 500 1 | C:360102 8PHIPPS B NP 500 360106 8SULLIVAN TN 500 1 | -707.6 | -1559
105.9421 | 4505.7155 | 4253 | -0.03813 | 242924 05HANG R 765 243208 05JEFRSO 765 1 | C:242928 05MARYSV 765 243206 05DUMONT 765 1 | -1370.4 | -4253
104.7932 | 4679.0153 | 4465 | -0.04042 | 242928 05MARYSV 765 243206 05DUMONT 765 1 | Base Case | -1355.4 | -4465
110.8435 | 4949.1642 | 4465 | -0.04134 | 242928 05MARYSV 765 243206 05DUMONT 765 1 | C:242935 05E LIMA 345 292438 T-130_TAP 345 1 | -1549.9 | -4465
112.3561 | 5016.6993 | 4465 | -0.04405 | 242928 05MARYSV 765 243206 05DUMONT 765 1 | C:243207 05GRNTWN 765 243208 05JEFRSO 765 1 | -1394.6 | -4465
121.7693 | 5437.0013 | 4465 | -0.04679 | 242928 05MARYSV 765 243206 05DUMONT 765 1 | C:242924 05HANG R 765 243208 05JEFRSO 765 1 | -1589.6 | -4465
165.9788 | 1488.8303 | 897 | -0.01564 | 242933 05CONVOY 345 243231 05ROB PK 345 1 | C:242928 05MARYSV 765 243206 05DUMONT 765 1 | 202.8 | -897
101.7709 | 1040.0987 | 1022 | 0.01136 | 242933 05CONVOY 345 296566 R60_TAP 345 1 | Base Case | 106 | 1022
112.3071 | 1147.779 | 1022 | 0.01189 | 242933 05CONVOY 345 296566 R60_TAP 345 1 | C:242928 05MARYSV 765 242939 05MARYSV 345 1 | 170.1 | 1022
114.8036 | 1173.293 | 1022 | 0.01248 | 242933 05CONVOY 345 296566 R60_TAP 345 1 | C:242924 05HANG R 765 243208 05JEFRSO 765 1 | 147.1 | 1022
145.4985 | 1486.9949 | 1022 | 0.01522 | 242933 05CONVOY 345 296566 R60_TAP 345 1 | C:242928 05MARYSV 765 243206 05DUMONT 765 1 | 235.5 | 1022
140.3564 | 2715.8966 | 1935 | 0.02254 | 243208 05JEFRSO 765 248000 06CLIFTY 345 1 | C:242924 05HANG R 765 243208 05JEFRSO 765 1 | 862.5 | 1935
115.1271 | 2158.6325 | 1875 | -0.02076 | 243210 05SULLVA 765 243213 05BREED 345 1 | C:243210 05SULLVA 765 243213 05BREED 345 2 | -451.6 | -1875
119.9816 | 2285.6495 | 1905 | -0.02198 | 243210 05SULLVA 765 243213 05BREED 345 2 | C:243210 05SULLVA 765 243213 05BREED 345 1 | -478.3 | -1905
189.251 | 2774.4192 | 1466 | -0.0296 | 243213 05BREED 345 346809 7CASEY 345 1 | Base Case | -340.5 | -1466
199.2648 | 2921.2214 | 1466 | -0.03005 | 243213 05BREED 345 346809 7CASEY 345 1 | C:270853 PONTI; R 345 348847 7BROKAW T1 345 1 | -450.3 | -1466
199.7764 | 2928.7218 | 1466 | -0.03014 | 243213 05BREED 345 346809 7CASEY 345 1 | C:270704 LORET; B 345 270926 WILTO; B 345 1 | -450.4 | -1466
210.3655 | 3083.9582 | 1466 | -0.03312 | 243213 05BREED 345 346809 7CASEY 345 1 | C:243221 05EUGENE 345 348885 7BUNSONVILLE 345 1 | -360.6 | -1466
103.0357 | 1451.7735 | 1409 | -0.01539 | 243214 05COLNGW 345 255105 17HIPLE 345 1 | C:242928 05MARYSV 765 243206 05DUMONT 765 1 | -186.3 | -1409
103.4876 | 1458.1399 | 1409 | -0.01533 | 243219 05DUMONT 345 243229 05OLIVE 345 2 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | -197.6 | -1409
227.8152 | 3209.9166 | 1409 | -0.02906 | 243219 05DUMONT 345 255113 17STLWEL 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | 820.4 | -1409
117.2078 | 1064.2467 | 908 | -0.0121 | 243221 05EUGENE 345 348885 7BUNSONVILLE 345 1 | Base Case | -69.3 | -908
138.9741 | 1261.8846 | 908 | -0.01306 | 243221 05EUGENE 345 348885 7BUNSONVILLE 345 1 | C:249503 08CAY CT 345 249505 08CAYUGA 345 1 | -188 | -908
154.5892 | 1403.6703 | 908 | -0.01705 | 243221 05EUGENE 345 348885 7BUNSONVILLE 345 1 | C:249521 08SUGCRK 345 347340 7KANSAS 345 1 | 1.7 | -908
182.1316 | 1653.7545 | 908 | -0.01839 | 243221 05EUGENE 345 348885 7BUNSONVILLE 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | -141.6 | -908
139.6546 | 1356.0461 | 971 | -0.0143 | 243229 05OLIVE 345 274804 UPNOR;RP 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | 180.2 | -971
184.9791 | 1796.1466 | 971 | -0.01906 | 243229 05OLIVE 345 274804 UPNOR;RP 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | 228.9 | -971
102.3538 | 1223.1274 | 1195 | -0.01272 | 249508 08DRESSR 345 249521 08SUGCRK 345 1 | C:249503 08CAY CT 345 249505 08CAYUGA 345 1 | -177.2 | -1195
106.8393 | 1276.7294 | 1195 | -0.01546 | 249508 08DRESSR 345 249521 08SUGCRK 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | -5.5 | -1195
130.5861 | 1800.782 | 1379 | -0.01948 | 270644 WILTO; 765 275233 WILTO;4M 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | 199 | -1379
120.6766 | 1374.5066 | 1139 | -0.01069 | 270664 B ISL; B 345 270666 B ISL;BT 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | -495.5 | -1139
101.4092 | 1499.8418 | 1479 | -0.0134 | 270665 B ISL; R 345 270667 B ISL;RT 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | -398 | -1479
138.5743 | 1996.8562 | 1441 | 0.01408 | 270678 BYRON; B 345 270694 CHERR; B 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 839.1 | 1441
169.9811 | 2449.4277 | 1441 | 0.0151 | 270678 BYRON; B 345 270694 CHERR; B 345 1 | C:270679 BYRON; R 345 270695 CHERR; R 345 1 | 1207.8 | 1441
189.4148 | 2729.4672 | 1441 | 0.01871 | 270678 BYRON; B 345 270694 CHERR; B 345 1 | C:270678 BYRON; B 345 270679 BYRON; R 345 1 | 1191 | 1441
118.8798 | 2051.8651 | 1726 | -0.02293 | 270678 BYRON; B 345 274768 LEECO;BP 345 1 | Base Case | -166.4 | -1726
132.098 | 2280.0121 | 1726 | -0.02578 | 270678 BYRON; B 345 274768 LEECO;BP 345 1 | C:601028 EAU CL 3 345 699244 ARP 345 345 1 | -160.2 | -1726
204.3872 | 3527.7234 | 1726 | -0.03746 | 270678 BYRON; B 345 274768 LEECO;BP 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | -447.5 | -1726
205.0368 | 3538.9343 | 1726 | -0.03742 | 270678 BYRON; B 345 274768 LEECO;BP 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | -462 | -1726
113.3029 | 1675.7495 | 1479 | 0.01035 | 270679 BYRON; R 345 270695 CHERR; R 345 1 | Base Case | 824.7 | 1479
142.0687 | 2101.1961 | 1479 | 0.01082 | 270679 BYRON; R 345 270695 CHERR; R 345 1 | C:270679 BYRON; R 345 270918 WEMPL; B 345 1 | 1211.5 | 1479
164.9345 | 2439.3817 | 1479 | 0.0171 | 270679 BYRON; R 345 270695 CHERR; R 345 1 | C:270694 CHERR; B 345 270695 CHERR; R 345 1 | 1033.3 | 1479
173.4586 | 2565.4534 | 1479 | 0.01583 | 270679 BYRON; R 345 270695 CHERR; R 345 1 | C:270678 BYRON; B 345 270694 CHERR; B 345 1 | 1263.8 | 1479
170.4498 | 2520.9526 | 1479 | 0.02032 | 270695 CHERR; R 345 270883 SILVE; R 345 1 | Base Case | 850.1 | 1479
172.1174 | 2545.616 | 1479 | 0.01963 | 270695 CHERR; R 345 270883 SILVE; R 345 1 | C:270918 WEMPL; B 345 270919 WEMPL; R 345 1 | 931.5 | 1479
226.4926 | 3349.825 | 1479 | 0.02848 | 270695 CHERR; R 345 270883 SILVE; R 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | 1008 | 1479
226.929 | 3356.2804 | 1479 | 0.02846 | 270695 CHERR; R 345 270883 SILVE; R 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 1016.1 | 1479
200.9205 | 2971.6137 | 1479 | 0.0331 | 270700 CORDO; B 345 270828 NELSO; B 345 1 | Base Case | 249.9 | 1479
264.864 | 3917.3386 | 1479 | 0.04528 | 270700 CORDO; B 345 270828 NELSO; B 345 1 | C:270864 QUAD3-11 345 270867 QUAD8-10 345 1 | 194.1 | 1479
335.4885 | 4961.8749 | 1479 | 0.05522 | 270700 CORDO; B 345 270828 NELSO; B 345 1 | C:270828 NELSO; B 345 270890 H471 ; 345 1 | 421.3 | 1479
335.5967 | 4963.4749 | 1479 | 0.05522 | 270700 CORDO; B 345 270828 NELSO; B 345 1 | C:270864 QUAD3-11 345 270890 H471 ; 345 1 | 422.9 | 1479
124.4988 | 1841.3366 | 1479 | -0.01928 | 270700 CORDO; B 345 270867 QUAD8-10 345 1 | C:270828 NELSO; B 345 270890 H471 ; 345 1 | -256 | -1479
124.5596 | 1842.2366 | 1479 | -0.01928 | 270700 CORDO; B 345 270867 QUAD8-10 345 1 | C:270864 QUAD3-11 345 270890 H471 ; 345 1 | -256.9 | -1479
194.43 | 2875.6195 | 1479 | -0.03198 | 270700 CORDO; B 345 270867 QUAD8-10 345 1 | C:270700 CORDO; B 345 274698 CORDO; 345 1 | -246 | -1479
146.2609 | 2237.7915 | 1530 | -0.02613 | 270700 CORDO; B 345 274698 CORDO; 345 1 | Base Case | -89.2 | -1530
192.6275 | 2947.2015 | 1530 | -0.03287 | 270700 CORDO; B 345 274698 CORDO; 345 1 | C:270700 CORDO; B 345 270867 QUAD8-10 345 1 | -244.4 | -1530
203.9568 | 3120.5384 | 1530 | -0.03594 | 270700 CORDO; B 345 274698 CORDO; 345 1 | C:270828 NELSO; B 345 270890 H471 ; 345 1 | -165.3 | -1530
204.0025 | 3121.2384 | 1530 | -0.03594 | 270700 CORDO; B 345 274698 CORDO; 345 1 | C:270864 QUAD3-11 345 270890 H471 ; 345 1 | -166 | -1530
140.6153 | 1735.1927 | 1234 | -0.0101 | 270704 LORET; B 345 270852 PONTI; B 345 1 | C:347288 7IPAVA 345 349661 7DUCK CRK 345 1 | -904.7 | -1234
141.4004 | 1744.8813 | 1234 | -0.01005 | 270704 LORET; B 345 270852 PONTI; B 345 1 | C:349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | -918.5 | -1234
143.0682 | 1765.4621 | 1234 | -0.01067 | 270704 LORET; B 345 270852 PONTI; B 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | -888.1 | -1234
104.938 | 1603.453 | 1528 | -0.01574 | 270713 DP 46; R 345 270857 PH117; R 345 1 | C:270940 ZION ; B 345 270941 ZION ; R 345 1 | -309.2 | -1528
130.4655 | 1394.6761 | 1069 | 0.01593 | 270728 E FRA; B 345 274750 CRETE;BP 345 1 | Base Case | 84.8 | 1069
152.5778 | 1631.0571 | 1069 | 0.01893 | 270728 E FRA; B 345 274750 CRETE;BP 345 1 | C:255109 17MUNSTR 345 270677 BURNH;0R 345 1 | 74.5 | 1069
153.5561 | 1641.5147 | 1069 | 0.01936 | 270728 E FRA; B 345 274750 CRETE;BP 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | 49.6 | 1069
193.7468 | 2071.1532 | 1069 | 0.02508 | 270728 E FRA; B 345 274750 CRETE;BP 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | -8.9 | 1069
122.0839 | 1805.6206 | 1479 | 0.01128 | 270730 ELECT; B 345 270812 LOMBA; B 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | 878.1 | 1479
123.3917 | 1824.9634 | 1479 | 0.01094 | 270730 ELECT; B 345 270812 LOMBA; B 345 1 | C:270678 BYRON; B 345 274768 LEECO;BP 345 1 | 925.4 | 1479
124.4108 | 1840.0362 | 1479 | 0.01223 | 270730 ELECT; B 345 270812 LOMBA; B 345 1 | C:270730 ELECT; B 345 270928 WOLFS; B 345 1 | 834.4 | 1479
283.0107 | 3398.9582 | 1201 | -0.03312 | 270730 ELECT; B 345 294490 P20 345 345 1 | Base Case | -675.6 | -1201
295.3203 | 3546.797 | 1201 | -0.03426 | 270730 ELECT; B 345 294490 P20 345 345 1 | C:270678 BYRON; B 345 270679 BYRON; R 345 1 | -729.7 | -1201
325.7517 | 3912.278 | 1201 | -0.03726 | 270730 ELECT; B 345 294490 P20 345 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | -848.5 | -1201
347.0098 | 4167.5882 | 1201 | -0.04171 | 270730 ELECT; B 345 294490 P20 345 345 1 | C:270678 BYRON; B 345 274768 LEECO;BP 345 1 | -737.9 | -1201
212.3602 | 1522.6224 | 717 | -0.01631 | 270796 KINCA; B 345 347962 7PAWNEE 345 1 | C:349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | 181.5 | -717
219.1679 | 1571.4341 | 717 | -0.01645 | 270796 KINCA; B 345 347962 7PAWNEE 345 1 | C:347288 7IPAVA 345 349661 7DUCK CRK 345 1 | 218.8 | -717
220.7757 | 1582.9616 | 717 | -0.01754 | 270796 KINCA; B 345 347962 7PAWNEE 345 1 | C:347945 7PANA 345 347962 7PAWNEE 345 1 | -140.7 | -717
103.2752 | 1240.3349 | 1201 | -0.01196 | 270806 LIBER; B 345 270940 ZION ; B 345 1 | C:270830 NB159; B 345 270940 ZION ; B 345 1 | -256.9 | -1201
108.6036 | 1606.2465 | 1479 | 0.01439 | 270807 LIBER; R 345 270857 PH117; R 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 423 | 1479
114.4718 | 1693.0373 | 1479 | 0.01479 | 270807 LIBER; R 345 270857 PH117; R 345 1 | C:270831 NB159; R 345 270942 ZION ;0B 345 1 | 476.9 | 1479
136.7158 | 2022.0267 | 1479 | 0.01721 | 270807 LIBER; R 345 270857 PH117; R 345 1 | C:270940 ZION ; B 345 270941 ZION ; R 345 1 | 606.9 | 1479
147.285 | 1964.7821 | 1334 | -0.01719 | 270807 LIBER; R 345 274817 ZIONE;RP 345 1 | C:270940 ZION ; B 345 270941 ZION ; R 345 1 | -551.3 | -1334
193.9159 | 2963.0351 | 1528 | -0.03293 | 270828 NELSO; B 345 270890 H471 ; 345 1 | Base Case | -255.3 | -1528
198.6177 | 3034.8784 | 1528 | -0.03268 | 270828 NELSO; B 345 270890 H471 ; 345 1 | C:274759 DELI 345 274768 LEECO;BP 345 1 | -347.7 | -1528
213.8255 | 3267.254 | 1528 | -0.03689 | 270828 NELSO; B 345 270890 H471 ; 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | -233.9 | -1528
324.3439 | 4955.9745 | 1528 | -0.05513 | 270828 NELSO; B 345 270890 H471 ; 345 1 | C:270700 CORDO; B 345 270828 NELSO; B 345 1 | -422.8 | -1528
139.1948 | 2058.6908 | 1479 | 0.02366 | 270828 NELSO; B 345 274768 LEECO;BP 345 1 | C:274759 DELI 345 274768 LEECO;BP 345 1 | -113.2 | 1479
169.727 | 2510.2624 | 1479 | 0.02468 | 270828 NELSO; B 345 274768 LEECO;BP 345 1 | Base Case | -480.9 | 1479
230.2996 | 3406.1316 | 1479 | 0.03917 | 270828 NELSO; B 345 274768 LEECO;BP 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | -185.3 | 1479
231.4957 | 3423.8207 | 1479 | 0.03921 | 270828 NELSO; B 345 274768 LEECO;BP 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | -199.7 | 1479
280.8875 | 3373.4587 | 1201 | 0.03321 | 270828 NELSO; B 345 294490 P20 345 345 1 | Base Case | 642.7 | 1201
293.1888 | 3521.1975 | 1201 | 0.03435 | 270828 NELSO; B 345 294490 P20 345 345 1 | C:270678 BYRON; B 345 270679 BYRON; R 345 1 | 696.7 | 1201
323.56 | 3885.9562 | 1201 | 0.03734 | 270828 NELSO; B 345 294490 P20 345 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | 815.6 | 1201
344.8099 | 4141.1663 | 1201 | 0.04179 | 270828 NELSO; B 345 294490 P20 345 345 1 | C:270678 BYRON; B 345 274768 LEECO;BP 345 1 | 704.9 | 1201
104.2381 | 1541.6808 | 1479 | -0.01692 | 270855 POWER; R 345 349662 7TAZEWELL 345 1 | C:270810 LOCKP; B 345 274702 KENDA;BU 345 1 | -150.4 | -1479
194.0664 | 2965.3351 | 1528 | 0.03293 | 270864 QUAD3-11 345 270890 H471 ; 345 1 | Base Case | 257.6 | 1528
198.7748 | 3037.2784 | 1528 | 0.03268 | 270864 QUAD3-11 345 270890 H471 ; 345 1 | C:274759 DELI 345 274768 LEECO;BP 345 1 | 350.1 | 1528
213.976 | 3269.554 | 1528 | 0.03689 | 270864 QUAD3-11 345 270890 H471 ; 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 236.2 | 1528
324.5009 | 4958.3745 | 1528 | 0.05513 | 270864 QUAD3-11 345 270890 H471 ; 345 1 | C:270700 CORDO; B 345 270828 NELSO; B 345 1 | 425.2 | 1528
236.1104 | 3473.1839 | 1471 | -0.03385 | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | Base Case | 689.8 | -1471
284.4246 | 4183.8856 | 1471 | -0.04117 | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | C:636600 SB 39 3 345 636635 OAKGROV3 345 1 | 798.6 | -1471
286.1358 | 4209.058 | 1471 | -0.04237 | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | C:636635 OAKGROV3 345 636640 LOUISA 3 345 1 | 725.1 | -1471
334.567 | 4921.4808 | 1471 | -0.04714 | 270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | C:636600 SB 39 3 345 636605 MECCORD3 345 1 | 1045.3 | -1471
156.3695 | 1671.5896 | 1069 | 0.01643 | 270867 QUAD8-10 345 636605 MECCORD3 345 1 | C:270828 NELSO; B 345 270890 H471 ; 345 1 | 320.6 | 1069
156.4537 | 1672.4896 | 1069 | 0.01643 | 270867 QUAD8-10 345 636605 MECCORD3 345 1 | C:270864 QUAD3-11 345 270890 H471 ; 345 1 | 321.5 | 1069
181.0606 | 1935.5381 | 1069 | -0.02193 | 270867 QUAD8-10 345 636605 MECCORD3 345 1 | C:270700 CORDO; B 345 274698 CORDO; 345 1 | 132.3 | -1069
113.9189 | 1368.1656 | 1201 | 0.01606 | 270883 SILVE; R 345 270917 WAYNE; R 345 1 | C:270807 LIBER; R 345 270883 SILVE; R 345 1 | -47.6 | 1201
135.0629 | 1622.1057 | 1201 | 0.01747 | 270883 SILVE; R 345 270917 WAYNE; R 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | -185.6 | 1201
135.4395 | 1626.628 | 1201 | 0.01748 | 270883 SILVE; R 345 270917 WAYNE; R 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | -189.3 | 1201
130.5861 | 1800.782 | 1379 | 0.01948 | 270927 WILTO; R 345 275233 WILTO;4M 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | -199 | 1379
116.0918 | 1394.2621 | 1201 | -0.01067 | 270941 ZION ; R 345 274817 ZIONE;RP 345 1 | C:270807 LIBER; R 345 274817 ZIONE;RP 345 1 | -516.9 | -1201
140.4113 | 1686.3396 | 1201 | -0.01295 | 270941 ZION ; R 345 274817 ZIONE;RP 345 1 | C:270941 ZION ; R 345 699432 PLS PR1 345 1 | -621.5 | -1201
106.2171 | 1622.9973 | 1528 | -0.01338 | 270941 ZION ; R 345 699432 PLS PR1 345 1 | C:270941 ZION ; R 345 274817 ZIONE;RP 345 1 | -522.8 | -1528
133.0388 | 2032.8329 | 1528 | -0.02085 | 270941 ZION ; R 345 699432 PLS PR1 345 1 | C:274817 ZIONE;RP 345 699432 PLS PR1 345 1 | -318.4 | -1528
108.1651 | 1156.2846 | 1069 | -0.01306 | 270942 ZION ;0B 345 699247 ARCADN3 345 1 | C:699253 ARCADN1 345 699432 PLS PR1 345 1 | -82.4 | -1069
112.75 | 1205.2977 | 1069 | -0.01347 | 270942 ZION ;0B 345 699247 ARCADN3 345 1 | C:699432 PLS PR1 345 699471 RACINE1 345 1 | -97.7 | -1069
132.0113 | 1411.2007 | 1069 | -0.0141 | 270942 ZION ;0B 345 699247 ARCADN3 345 1 | C:270940 ZION ; B 345 270941 ZION ; R 345 1 | -251.8 | -1069
101.1152 | 1556.1624 | 1539 | -0.01772 | 274817 ZIONE;RP 345 699432 PLS PR1 345 1 | C:270942 ZION ;0B 345 699247 ARCADN3 345 1 | -99.1 | -1539
102.6087 | 1579.1472 | 1539 | -0.01686 | 274817 ZIONE;RP 345 699432 PLS PR1 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | -192.8 | -1539
137.0259 | 2108.8281 | 1539 | -0.02215 | 274817 ZIONE;RP 345 699432 PLS PR1 345 1 | C:270941 ZION ; R 345 699432 PLS PR1 345 1 | -287.5 | -1539
114.8815 | 3933.542 | 3424 | 0.01111 | 314901 8BATH CO 500 314912 8LEXNGTN 500 1 | C:314901 8BATH CO 500 314926 8VALLEY 500 1 | 3020 | 3424
114.8815 | 3933.542 | 3424 | 0.01111 | 314901 8BATH CO 500 314926 8VALLEY 500 1 | C:314901 8BATH CO 500 314912 8LEXNGTN 500 1 | 3020 | 3424
118.945 | 4072.6755 | 3424 | 0.01813 | 314901 8BATH CO 500 314926 8VALLEY 500 1 | C:314907 8DOOMS 500 314912 8LEXNGTN 500 1 | 2581.9 | 3424
129.216 | 3764.0607 | 2913 | -0.01736 | 314907 8DOOMS 500 314912 8LEXNGTN 500 1 | C:314901 8BATH CO 500 314926 8VALLEY 500 1 | -2336.6 | -2913
107.7001 | 2798.0482 | 2598 | -0.01008 | 314908 8ELMONT 500 314910 8CUNNING 500 1 | C:293013 U2-068 TAP 500 314926 8VALLEY 500 1 | -1969.2 | -2598
107.9982 | 2805.7927 | 2598 | -0.0101 | 314908 8ELMONT 500 314910 8CUNNING 500 1 | C:293013 U2-068 TAP 500 314917 8MT STM 500 1 | -1975.3 | -2598
MISO
125.4934 | 1439.4089 | 1147 | -0.01581 | 255107 17LKGORG 345 255109 17MUNSTR 345 1 | C:255112 17STJOHN 345 274750 CRETE;BP 345 1 | 139.4 | -1147
168.7115 | 1935.1207 | 1147 | -0.02062 | 255107 17LKGORG 345 255109 17MUNSTR 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | 239.6 | -1147
115.404 | 1233.6688 | 1069 | -0.0144 | 255109 17MUNSTR 345 270677 BURNH;0R 345 1 | Base Case | 49.6 | -1069
144.7572 | 1547.455 | 1069 | -0.01848 | 255109 17MUNSTR 345 270677 BURNH;0R 345 1 | C:270728 E FRA; B 345 274750 CRETE;BP 345 1 | 27.9 | -1069
147.8382 | 1580.3903 | 1069 | -0.0189 | 255109 17MUNSTR 345 270677 BURNH;0R 345 1 | C:255112 17STJOHN 345 274750 CRETE;BP 345 1 | 26.3 | -1069
196.1129 | 2096.4467 | 1069 | -0.02373 | 255109 17MUNSTR 345 270677 BURNH;0R 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | 145.2 | -1069
114.4713 | 1223.6981 | 1069 | -0.01356 | 255111 17SHEFLD 345 270674 BURNH; B 345 1 | C:270728 E FRA; B 345 274750 CRETE;BP 345 1 | -108.7 | -1069
116.8818 | 1249.4662 | 1069 | -0.01386 | 255111 17SHEFLD 345 270674 BURNH; B 345 1 | C:255112 17STJOHN 345 274750 CRETE;BP 345 1 | -109.8 | -1069
138.3522 | 1478.9847 | 1069 | -0.01773 | 255111 17SHEFLD 345 270674 BURNH; B 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | -21.1 | -1069
140.8387 | 1536.5507 | 1091 | -0.01758 | 255112 17STJOHN 345 274750 CRETE;BP 345 1 | Base Case | -91 | -1091
162.5052 | 1772.9317 | 1091 | -0.02058 | 255112 17STJOHN 345 274750 CRETE;BP 345 1 | C:255109 17MUNSTR 345 270677 BURNH;0R 345 1 | -80.7 | -1091
163.4637 | 1783.3893 | 1091 | -0.02101 | 255112 17STJOHN 345 274750 CRETE;BP 345 1 | C:270607 COLLI; 765 270644 WILTO; 765 1 | -55.8 | -1091
201.632 | 2199.8054 | 1091 | -0.02672 | 255112 17STJOHN 345 274750 CRETE;BP 345 1 | C:243206 05DUMONT 765 270644 WILTO; 765 1 | 2.7 | -1091
108.6158 | 1555.3789 | 1432 | -0.01885 | 344102 7BELLEAU 345 344535 7ENON 345 1 | Base Case | -5.4 | -1432
124.336 | 1780.4918 | 1432 | -0.02155 | 344102 7BELLEAU 345 344535 7ENON 345 1 | C:345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | -8.5 | -1432
129.9796 | 1861.3075 | 1432 | -0.0225 | 344102 7BELLEAU 345 344535 7ENON 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | 11.2 | -1432
135.9568 | 1946.9009 | 1432 | -0.02344 | 344102 7BELLEAU 345 344535 7ENON 345 1 | C:344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | 19.5 | -1432
138.7347 | 1986.6814 | 1432 | 0.02168 | 344102 7BELLEAU 345 345747 7SIOUX 345 1 | C:347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | -204 | 1432
140.358 | 2009.9272 | 1432 | 0.02197 | 344102 7BELLEAU 345 345747 7SIOUX 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | -203.4 | 1432
145.3971 | 2082.0865 | 1432 | 0.02276 | 344102 7BELLEAU 345 345747 7SIOUX 345 1 | C:344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | -210.6 | 1432
128.1846 | 1531.8066 | 1195 | 0.01765 | 344154 7BLAND 345 344885 7LABADIE2 345 1 | Base Case | -80.5 | 1195
145.4774 | 1738.4552 | 1195 | 0.02086 | 344154 7BLAND 345 344885 7LABADIE2 345 1 | C:344535 7ENON 345 345230 7MONTGMRY 345 1 | -23.2 | 1195
148.8209 | 1778.4098 | 1195 | 0.02066 | 344154 7BLAND 345 344885 7LABADIE2 345 1 | C:344102 7BELLEAU 345 344535 7ENON 345 1 | -79.6 | 1195
174.4735 | 2084.9589 | 1195 | 0.02396 | 344154 7BLAND 345 344885 7LABADIE2 345 1 | C:344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | -114.8 | 1195
174.1378 | 1664.7573 | 956 | -0.01664 | 344535 7ENON 345 345230 7MONTGMRY 345 1 | Base Case | -296.5 | -956
198.9102 | 1901.582 | 956 | -0.01948 | 344535 7ENON 345 345230 7MONTGMRY 345 1 | C:345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | -299.8 | -956
203.3004 | 1943.5522 | 956 | -0.02023 | 344535 7ENON 345 345230 7MONTGMRY 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | -280.1 | -956
212.6176 | 2032.6246 | 956 | -0.02143 | 344535 7ENON 345 345230 7MONTGMRY 345 1 | C:344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | -270.5 | -956
129.2677 | 1544.7495 | 1195 | 0.01502 | 344822 7JOACHIM 345 345668 7RUSH 2 345 1 | C:345667 7RUSH 1 345 345857 7TYSON 3 345 1 | 309.7 | 1195
118.7164 | 1418.6615 | 1195 | -0.01287 | 344822 7JOACHIM 345 345858 7TYSON 1 345 1 | C:345747 7SIOUX 345 348151 7ROXFORD 345 1 | -360.4 | -1195
121.3013 | 1449.5507 | 1195 | -0.01062 | 344822 7JOACHIM 345 345858 7TYSON 1 345 1 | C:345857 7TYSON 3 345 345859 7TYSON 2 345 1 | -576.3 | -1195
147.8712 | 1767.0609 | 1195 | -0.01507 | 344822 7JOACHIM 345 345858 7TYSON 1 345 1 | C:345667 7RUSH 1 345 345857 7TYSON 3 345 1 | -527.9 | -1195
153.1715 | 1410.7099 | 921 | -0.0137 | 344849 7KELSO 345 344974 7LUTESVIL 345 1 | Base Case | -284.2 | -921
168.6214 | 1553.0028 | 921 | -0.01455 | 344849 7KELSO 345 344974 7LUTESVIL 345 1 | C:346992 7E W FKFT 345 348827 7W MT VERNON 345 1 | -356.6 | -921
169.2644 | 1558.9251 | 921 | -0.01456 | 344849 7KELSO 345 344974 7LUTESVIL 345 1 | C:346992 7E W FKFT 345 360002 7SHAWNEE FP 345 1 | -361.7 | -921
183.3746 | 1688.88 | 921 | -0.01674 | 344849 7KELSO 345 344974 7LUTESVIL 345 1 | C:348773 7PR STATE 345 348827 7W MT VERNON 345 1 | -312.4 | -921
108.125 | 1376.4316 | 1273 | 0.01591 | 344849 7KELSO 345 347325 7JOPPA TS 345 1 | Base Case | 68.2 | 1273
130.538 | 1661.7488 | 1273 | 0.01951 | 344849 7KELSO 345 347325 7JOPPA TS 345 1 | C:338187 8DELL 5 500 338188 8SANSOUCI 500 1 | 57.5 | 1273
130.538 | 1661.7488 | 1273 | 0.01951 | 344849 7KELSO 345 347325 7JOPPA TS 345 1 | C:338188 8SANSOUCI 500 360021 8SHELBY TN 500 1 | 57.5 | 1273
131.3452 | 1672.0248 | 1273 | 0.01914 | 344849 7KELSO 345 347325 7JOPPA TS 345 1 | C:348773 7PR STATE 345 348827 7W MT VERNON 345 1 | 98.2 | 1273
121.4794 | 1451.6791 | 1195 | -0.01656 | 344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | Base Case | 90 | -1195
147.6822 | 1764.8023 | 1195 | -0.02142 | 344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | C:344535 7ENON 345 345230 7MONTGMRY 345 1 | 3.5 | -1195
150.8982 | 1803.233 | 1195 | -0.02085 | 344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | C:344102 7BELLEAU 345 344535 7ENON 345 1 | 88.8 | -1195
173.406 | 2072.2022 | 1195 | -0.02371 | 344886 7LABADIE3 345 345230 7MONTGMRY 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | 122.6 | -1195
103.4204 | 1235.8739 | 1195 | -0.01081 | 344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | C:300040 7FLETCH 345 300047 7SALEM 345 1 | -347 | -1195
103.8604 | 1241.1319 | 1195 | -0.01133 | 344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | C:300051 7STFRANCISTP 345 300054 7GOBKNOB 345 1 | -309.5 | -1195
116.363 | 1390.5375 | 1195 | -0.0125 | 344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | C:348773 7PR STATE 345 348827 7W MT VERNON 345 1 | -362.7 | -1195
107.0893 | 1279.7168 | 1195 | 0.01514 | 345045 7MASON 1 345 345747 7SIOUX 345 1 | C:344102 7BELLEAU 345 345747 7SIOUX 345 1 | -34.8 | 1195
236.2633 | 2818.6213 | 1193 | 0.03005 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | Base Case | -347.7 | 1193
254.6345 | 3037.7893 | 1193 | 0.03264 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -353.9 | 1193
255.4438 | 3047.4447 | 1193 | 0.03262 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | C:300042 7HUBEN 345 300045 7MORGAN 345 1 | -365.2 | 1193
261.3778 | 3118.2377 | 1193 | 0.03347 | 345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | -366.1 | 1193
208.2008 | 1917.5289 | 921 | -0.02233 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | Base Case | 81.4 | -921
221.7113 | 2041.9615 | 921 | -0.0245 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | C:3Wnd: OPEN B$0233 1 | 27.4 | -921
227.7712 | 2097.7724 | 921 | -0.02446 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 86.5 | -921
230.7499 | 2125.2069 | 921 | -0.0247 | 345088 7MCCREDIE 345 345408 7OVERTON 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 94.2 | -921
125.3069 | 1132.7747 | 904 | -0.01099 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | C:347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | -229.1 | -904
131.7892 | 1191.3743 | 904 | -0.0109 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | C:345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | -295.1 | -904
219.3409 | 2096.8994 | 956 | -0.02546 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | Base Case | 3.4 | -956
233.5873 | 2233.095 | 956 | -0.02685 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | C:300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | -25.3 | -956
240.8589 | 2302.611 | 956 | -0.02789 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 9.3 | -956
242.8139 | 2321.3005 | 956 | -0.02802 | 345408 7OVERTON 345 541201 SIBLEY 7 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 17.3 | -956
416.6643 | 1249.9928 | 300 | 0.01477 | 345408 7OVERTON 345 B$0233 1.00 1 | C:345088 7MCCREDIE 345 345408 7OVERTON 345 1 | 35.5 | 300
131.0864 | 2350.3791 | 1793 | 0.02819 | 345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | Base Case | 32.4 | 1793
140.2319 | 2514.3582 | 1793 | 0.02845 | 345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | C:345230 7MONTGMRY 345 345992 7SPENCER 345 1 | 175 | 1793
143.0898 | 2565.6004 | 1793 | 0.03031 | 345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | 73.3 | 1793
143.1611 | 2566.8781 | 1793 | 0.0303 | 345435 7PALM TAP 345 348060 7SE QUINCY 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 75.4 | 1793
264.5201 | 2401.8421 | 908 | -0.02741 | 345435 7PALM TAP 345 636645 SUB T 3 345 1 | Base Case | 148 | -908
284.7309 | 2585.3563 | 908 | -0.03038 | 345435 7PALM TAP 345 636645 SUB T 3 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 87.3 | -908
285.1408 | 2589.0785 | 908 | -0.03039 | 345435 7PALM TAP 345 636645 SUB T 3 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | 90.2 | -908
292.6689 | 2657.434 | 908 | -0.03037 | 345435 7PALM TAP 345 636645 SUB T 3 345 1 | C:636635 OAKGROV3 345 636640 LOUISA 3 345 1 | 160.2 | -908
110.8085 | 1324.1611 | 1195 | -0.01278 | 345667 7RUSH 1 345 345857 7TYSON 3 345 1 | C:345747 7SIOUX 345 348151 7ROXFORD 345 1 | -273.3 | -1195
128.4883 | 1535.4352 | 1195 | -0.01434 | 345667 7RUSH 1 345 345857 7TYSON 3 345 1 | C:344822 7JOACHIM 345 345668 7RUSH 2 345 1 | -356.3 | -1195
139.7483 | 1669.9919 | 1195 | -0.01459 | 345667 7RUSH 1 345 345857 7TYSON 3 345 1 | C:344822 7JOACHIM 345 345858 7TYSON 1 345 1 | -470.3 | -1195
159.3138 | 2271.8151 | 1426 | 0.02641 | 345747 7SIOUX 345 348151 7ROXFORD 345 1 | Base Case | -100.2 | 1426
180.8578 | 2579.0327 | 1426 | 0.0301 | 345747 7SIOUX 345 348151 7ROXFORD 345 1 | C:345668 7RUSH 2 345 345669 7RUSH 3 345 1 | -104 | 1426
182.6531 | 2604.6327 | 1426 | 0.0301 | 345747 7SIOUX 345 348151 7ROXFORD 345 1 | C:345669 7RUSH 3 345 348774 7BALDWIN 345 1 | -129.6 | 1426
188.0547 | 2681.6597 | 1426 | 0.0311 | 345747 7SIOUX 345 348151 7ROXFORD 345 1 | C:347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | -124.4 | 1426
143.4269 | 1713.9518 | 1195 | 0.02014 | 346809 7CASEY 345 347340 7KANSAS 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | 57.9 | 1195
156.5651 | 1870.9524 | 1195 | -0.01794 | 346809 7CASEY 345 347821 7NEOGA 345 1 | Base Case | -395.8 | -1195
178.4266 | 2132.198 | 1195 | -0.02052 | 346809 7CASEY 345 347821 7NEOGA 345 1 | C:347945 7PANA 345 348961 7MTZION 345 1 | -444.9 | -1195
188.6807 | 2254.7341 | 1195 | -0.02341 | 346809 7CASEY 345 347821 7NEOGA 345 1 | C:346809 7CASEY 345 347830 7NEWTON 345 1 | -329.8 | -1195
189.5197 | 2264.7604 | 1195 | -0.02194 | 346809 7CASEY 345 347821 7NEOGA 345 1 | C:347340 7KANSAS 345 348961 7MTZION 345 1 | -460.7 | -1195
137.8996 | 1647.9004 | 1195 | -0.01868 | 346809 7CASEY 345 347830 7NEWTON 345 1 | C:347821 7NEOGA 345 348491 7HOLLAND 345 1 | 111.9 | -1195
146.5121 | 1750.8199 | 1195 | -0.02044 | 346809 7CASEY 345 347830 7NEWTON 345 1 | C:346809 7CASEY 345 347821 7NEOGA 345 1 | 70.1 | -1195
147.2134 | 1759.2004 | 1195 | -0.01868 | 346809 7CASEY 345 347830 7NEWTON 345 1 | C:348067 7RAMSEY 345 348491 7HOLLAND 345 1 | 223.2 | -1195
102.2408 | 1221.778 | 1195 | -0.014 | 346886 7COFFEN N 345 346895 7COFFEEN 345 1 | C:346886 7COFFEN N 345 346895 7COFFEEN 345 2 | -70.6 | -1195
102.2408 | 1221.778 | 1195 | -0.014 | 346886 7COFFEN N 345 346895 7COFFEEN 345 2 | C:346886 7COFFEN N 345 346895 7COFFEEN 345 1 | -70.6 | -1195
134.6651 | 1609.2485 | 1195 | 0.01713 | 346886 7COFFEN N 345 348067 7RAMSEY 345 1 | Base Case | -200.7 | 1195
153.2838 | 1831.7409 | 1195 | 0.02018 | 346886 7COFFEN N 345 348067 7RAMSEY 345 1 | C:348773 7PR STATE 345 348827 7W MT VERNON 345 1 | -172.4 | 1195
153.4057 | 1833.198 | 1195 | 0.02052 | 346886 7COFFEN N 345 348067 7RAMSEY 345 1 | C:347340 7KANSAS 345 348961 7MTZION 345 1 | -145.9 | 1195
158.7976 | 1897.6317 | 1195 | 0.02058 | 346886 7COFFEN N 345 348067 7RAMSEY 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | -205.4 | 1195
173.6575 | 2075.2077 | 1195 | -0.02021 | 346895 7COFFEEN 345 348151 7ROXFORD 345 1 | Base Case | 413.4 | -1195
198.9849 | 2377.8694 | 1195 | -0.02383 | 346895 7COFFEEN 345 348151 7ROXFORD 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | 418.4 | -1195
201.1238 | 2403.4292 | 1195 | -0.02471 | 346895 7COFFEEN 345 348151 7ROXFORD 345 1 | C:348773 7PR STATE 345 348827 7W MT VERNON 345 1 | 371.6 | -1195
209.7832 | 2506.9091 | 1195 | -0.02515 | 346895 7COFFEEN 345 348151 7ROXFORD 345 1 | C:347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | 438.9 | -1195
107.7579 | 1287.7066 | 1195 | -0.01069 | 346992 7E W FKFT 345 348827 7W MT VERNON 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | -408.7 | -1195
234.3896 | 1680.5731 | 717 | 0.0153 | 347288 7IPAVA 345 349661 7DUCK CRK 345 1 | Base Case | 422.5 | 717
243.5061 | 1745.9391 | 717 | 0.01515 | 347288 7IPAVA 345 349661 7DUCK CRK 345 1 | C:270717 DRESD; R 345 270853 PONTI; R 345 1 | 500.2 | 717
248.4174 | 1781.1526 | 717 | 0.01565 | 347288 7IPAVA 345 349661 7DUCK CRK 345 1 | C:270704 LORET; B 345 270926 WILTO; B 345 1 | 494.3 | 717
251.3385 | 1802.0971 | 717 | 0.01567 | 347288 7IPAVA 345 349661 7DUCK CRK 345 1 | C:270853 PONTI; R 345 348847 7BROKAW T1 345 1 | 513.6 | 717
113.2145 | 1082.3306 | 956 | 0.01106 | 347340 7KANSAS 345 348887 7SIDNEY 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | 172.9 | 956
102.4701 | 1837.2882 | 1793 | -0.01845 | 347340 7KANSAS 345 348961 7MTZION 345 1 | C:346809 7CASEY 345 347821 7NEOGA 345 1 | -320.2 | -1793
107.017 | 1918.8143 | 1793 | -0.01927 | 347340 7KANSAS 345 348961 7MTZION 345 1 | C:347821 7NEOGA 345 348491 7HOLLAND 345 1 | -334.3 | -1793
143.6269 | 2575.2297 | 1793 | -0.02947 | 347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | Base Case | 152 | -1793
151.2175 | 2711.3291 | 1793 | -0.03167 | 347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 107.2 | -1793
151.3402 | 2713.5291 | 1793 | -0.03167 | 347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | 109.4 | -1793
161.6075 | 2897.6225 | 1793 | -0.03261 | 347679 7MEREDOSIA 345 348060 7SE QUINCY 345 1 | C:346895 7COFFEEN 345 348151 7ROXFORD 345 1 | 216.2 | -1793
171.0872 | 1851.1633 | 1082 | -0.0179 | 347821 7NEOGA 345 348491 7HOLLAND 345 1 | Base Case | -379.3 | -1082
195.4116 | 2114.3535 | 1082 | -0.0205 | 347821 7NEOGA 345 348491 7HOLLAND 345 1 | C:347945 7PANA 345 348961 7MTZION 345 1 | -428.7 | -1082
200.6823 | 2171.3822 | 1082 | -0.02186 | 347821 7NEOGA 345 348491 7HOLLAND 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | -373.9 | -1082
207.3705 | 2243.749 | 1082 | -0.02189 | 347821 7NEOGA 345 348491 7HOLLAND 345 1 | C:347340 7KANSAS 345 348961 7MTZION 345 1 | -443.8 | -1082
115.366 | 1378.6232 | 1195 | -0.01649 | 347830 7NEWTON 345 348493 7XENIA 345 1 | Base Case | 22.7 | -1195
131.4446 | 1570.7633 | 1195 | -0.0179 | 347830 7NEWTON 345 348493 7XENIA 345 1 | C:346992 7E W FKFT 345 348827 7W MT VERNON 345 1 | -98.9 | -1195
132.0801 | 1578.3567 | 1195 | -0.01884 | 347830 7NEWTON 345 348493 7XENIA 345 1 | C:346809 7CASEY 345 347821 7NEOGA 345 1 | -29.2 | -1195
138.9172 | 1660.0605 | 1195 | -0.01965 | 347830 7NEWTON 345 348493 7XENIA 345 1 | C:347821 7NEOGA 345 348491 7HOLLAND 345 1 | -44.3 | -1195
154.821 | 1675.1633 | 1082 | 0.0179 | 348067 7RAMSEY 345 348491 7HOLLAND 345 1 | Base Case | -203.3 | 1082
170.0049 | 1839.4535 | 1082 | 0.0205 | 348067 7RAMSEY 345 348491 7HOLLAND 345 1 | C:347945 7PANA 345 348961 7MTZION 345 1 | -153.8 | 1082
179.1727 | 1938.649 | 1082 | 0.02189 | 348067 7RAMSEY 345 348491 7HOLLAND 345 1 | C:347340 7KANSAS 345 348961 7MTZION 345 1 | -138.7 | 1082
185.4143 | 2006.1822 | 1082 | 0.02186 | 348067 7RAMSEY 345 348491 7HOLLAND 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | -208.7 | 1082
141.8128 | 1694.6633 | 1195 | -0.0179 | 348493 7XENIA 345 348827 7W MT VERNON 345 1 | C:346992 7E W FKFT 345 348827 7W MT VERNON 345 1 | 222.8 | -1195
154.1052 | 1841.5567 | 1195 | -0.01884 | 348493 7XENIA 345 348827 7W MT VERNON 345 1 | C:346809 7CASEY 345 347821 7NEOGA 345 1 | 292.4 | -1195
158.4151 | 1893.0606 | 1195 | -0.01965 | 348493 7XENIA 345 348827 7W MT VERNON 345 1 | C:347821 7NEOGA 345 348491 7HOLLAND 345 1 | 277.3 | -1195
163.6394 | 1955.491 | 1195 | 0.02137 | 348773 7PR STATE 345 348827 7W MT VERNON 345 1 | Base Case | 198.3 | 1195
181.5482 | 2169.5009 | 1195 | 0.02344 | 348773 7PR STATE 345 348827 7W MT VERNON 345 1 | C:347821 7NEOGA 345 348491 7HOLLAND 345 1 | 242.1 | 1195
182.861 | 2185.1891 | 1195 | 0.0233 | 348773 7PR STATE 345 348827 7W MT VERNON 345 1 | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 269.3 | 1195
183.1886 | 2189.1039 | 1195 | 0.02407 | 348773 7PR STATE 345 348827 7W MT VERNON 345 1 | C:344849 7KELSO 345 347325 7JOPPA TS 345 1 | 209.9 | 1195
100.2966 | 910.6931 | 908 | -0.01019 | 348885 7BUNSONVILLE 345 348887 7SIDNEY 345 1 | Base Case | -72.8 | -908
120.2346 | 1091.7306 | 908 | -0.01106 | 348885 7BUNSONVILLE 345 348887 7SIDNEY 345 1 | C:249503 08CAY CT 345 249505 08CAYUGA 345 1 | -182.3 | -908
135.266 | 1228.2155 | 908 | -0.01487 | 348885 7BUNSONVILLE 345 348887 7SIDNEY 345 1 | C:249521 08SUGCRK 345 347340 7KANSAS 345 1 | -5.5 | -908
162.1292 | 1472.1329 | 908 | -0.01618 | 348885 7BUNSONVILLE 345 348887 7SIDNEY 345 1 | C:243213 05BREED 345 346809 7CASEY 345 1 | -141.7 | -908
149.2797 | 1783.8928 | 1195 | 0.01477 | 349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | Base Case | 569.4 | 1195
159.5179 | 1906.2391 | 1195 | 0.01515 | 349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | C:270853 PONTI; R 345 348847 7BROKAW T1 345 1 | 660.5 | 1195
166.7078 | 1992.1581 | 1195 | 0.01682 | 349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | 609.1 | 1195
166.8063 | 1993.3359 | 1195 | 0.01681 | 349661 7DUCK CRK 345 349740 7MAPLE RIDGE 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | 611.1 | 1195
121.7083 | 1454.4138 | 1195 | -0.01451 | 349662 7TAZEWELL 345 349740 7MAPLE RIDGE 345 1 | Base Case | -261.3 | -1195
141.1727 | 1687.0136 | 1195 | -0.0168 | 349662 7TAZEWELL 345 349740 7MAPLE RIDGE 345 1 | C:270828 NELSO; B 345 294490 P20 345 345 1 | -305.6 | -1195
141.3652 | 1689.3136 | 1195 | -0.0168 | 349662 7TAZEWELL 345 349740 7MAPLE RIDGE 345 1 | C:270730 ELECT; B 345 294490 P20 345 345 1 | -307.9 | -1195
145.4248 | 1737.826 | 1195 | -0.01474 | 349662 7TAZEWELL 345 349740 7MAPLE RIDGE 345 1 | C:349730 7FARGO 345 349740 7MAPLE RIDGE 345 1 | -525.8 | -1195
100.72 | 1204.1073 | 1195.5 | -0.01316 | 601014 AS KING3 345 601021 KOLMNLK3 345 1 | C:601014 AS KING3 345 601023 REDROCK3 345 1 | -122 | -1195.5
111.1895 | 1329.27 | 1195.5 | -0.01 | 601014 AS KING3 345 601023 REDROCK3 345 1 | Base Case | -507 | -1195.5
122.1112 | 1459.839 | 1195.5 | -0.01048 | 601014 AS KING3 345 601023 REDROCK3 345 1 | C:601019 COON CK3 345 615353 GRE-DICKNSN3 345 1 | -598.1 | -1195.5
124.8796 | 1492.9353 | 1195.5 | -0.01205 | 601014 AS KING3 345 601023 REDROCK3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -502.1 | -1195.5
125.2229 | 1497.0396 | 1195.5 | -0.01295 | 601014 AS KING3 345 601023 REDROCK3 345 1 | C:601014 AS KING3 345 601021 KOLMNLK3 345 1 | -432.2 | -1195.5
116.7297 | 1394.9202 | 1195 | 0.01586 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | Base Case | 90.8 | 1195
128.3594 | 1533.8943 | 1195 | 0.01742 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | C:699449 ARROWHD 345 699450 ST LAKE 345 1 | 101.5 | 1195
132.7019 | 1585.7877 | 1195 | 0.01836 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | C:699450 ST LAKE 345 699676 GARDR PK 345 1 | 76.1 | 1195
134.0929 | 1602.4104 | 1195 | 0.01846 | 601014 AS KING3 345 601028 EAU CL 3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 84.5 | 1195
153.3262 | 1832.2482 | 1195 | 0.02171 | 601028 EAU CL 3 345 699244 ARP 345 345 1 | Base Case | -47.1 | 1195
162.277 | 1939.2105 | 1195 | 0.02313 | 601028 EAU CL 3 345 699244 ARP 345 345 1 | C:699449 ARROWHD 345 699450 ST LAKE 345 1 | -37.3 | 1195
178.396 | 2131.8317 | 1195 | 0.02525 | 601028 EAU CL 3 345 699244 ARP 345 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -55.6 | 1195
188.9376 | 2257.8046 | 1195 | 0.02654 | 601028 EAU CL 3 345 699244 ARP 345 345 1 | C:699450 ST LAKE 345 699676 GARDR PK 345 1 | -75.5 | 1195
137.9101 | 1272.9103 | 923 | 0.01379 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | Base Case | -139 | 923
161.5398 | 1491.0127 | 923 | 0.01662 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | -124.4 | 923
197.6351 | 1824.1723 | 923 | 0.01979 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | C:700528 MITCHLCO 765 765 700543 HILLS 3 765 765 N1 | -196.9 | 923
299.8742 | 2767.8392 | 923 | 0.03145 | 631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -181.8 | 923
129.0159 | 1126.309 | 873 | -0.01352 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | C:631139 HAZLTON3 345 636000 WEBSTER3 345 N1 | -14.6 | -873
155.1963 | 1354.8639 | 873 | -0.0157 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | C:700528 MITCHLCO 765 765 700543 HILLS 3 765 765 N1 | 63.9 | -873
211.5342 | 1846.694 | 873 | -0.022 | 631139 HAZLTON3 345 631144 MITCHLCO3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 37.7 | -873
130.6317 | 1255.3705 | 961 | 0.01476 | 631142 ARNOLD 3 345 631148 MORGANV3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | -41.7 | 961
160.7671 | 1544.9721 | 961 | 0.01741 | 631142 ARNOLD 3 345 631148 MORGANV3 345 1 | C:700528 MITCHLCO 765 765 700543 HILLS 3 765 765 N1 | -113.4 | 961
262.667 | 2524.2297 | 961 | 0.02947 | 631142 ARNOLD 3 345 631148 MORGANV3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -101 | 961
136.335 | 1310.1793 | 961 | 0.01427 | 631148 MORGANV3 345 636420 TIFFIN 3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | -136.8 | 961
167.2925 | 1607.6808 | 961 | 0.01692 | 631148 MORGANV3 345 636420 TIFFIN 3 345 1 | C:700528 MITCHLCO 765 765 700543 HILLS 3 765 765 N1 | -216.4 | 961
283.4064 | 2723.5353 | 961 | 0.03064 | 631148 MORGANV3 345 636420 TIFFIN 3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -204.1 | 961
112.8045 | 1299.5076 | 1152 | 0.01554 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 21.7 | 1152
109.3263 | 1259.4386 | 1152 | 0.01506 | 635600 GRIMES 3 345 635700 SYCAMOR3 345 2 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 21.1 | 1152
136.6264 | 1573.9359 | 1152 | -0.01681 | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | 191.7 | -1152
214.1373 | 2466.8613 | 1152 | -0.02679 | 635680 BONDRNT3 345 635700 SYCAMOR3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 264 | -1152
119.463 | 1142.0662 | 956 | 0.01386 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | Base Case | -2.4 | 956
142.3442 | 1360.8102 | 956 | 0.01608 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | C:631143 OTTUMWA3 345 700399 MO-C STA 345 345 N1 | 38.6 | 956
178.383 | 1705.3417 | 956 | 0.02036 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | 31.2 | 956
284.592 | 2720.6998 | 956 | 0.03251 | 635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -47.5 | 956
121.8486 | 1164.8728 | 956 | 0.01292 | 635730 MNTZUMA3 345 636400 HILLS 3 345 1 | Base Case | 102.5 | 956
143.2587 | 1369.553 | 956 | 0.01574 | 635730 MNTZUMA3 345 636400 HILLS 3 345 1 | C:700528 MITCHLCO 765 765 700543 HILLS 3 765 765 N1 | 75.3 | 956
182.0972 | 1740.8488 | 956 | 0.01951 | 635730 MNTZUMA3 345 636400 HILLS 3 345 1 | C:700542 GRIMES 3 765 765 700543 HILLS 3 765 765 N1 | 136.6 | 956
285.8066 | 2732.3111 | 956 | 0.03256 | 635730 MNTZUMA3 345 636400 HILLS 3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 55 | 956
263.0502 | 2688.3729 | 1022 | -0.02922 | 636400 HILLS 3 345 636420 TIFFIN 3 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 285.7 | -1022
317.1337 | 4135.4232 | 1304 | 0.04671 | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | Base Case | -294.6 | 1304
334.6117 | 4363.3361 | 1304 | 0.04941 | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | C:601028 EAU CL 3 345 699244 ARP 345 345 1 | -300.5 | 1304
385.9121 | 5032.2932 | 1304 | 0.05671 | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | C:636640 LOUISA 3 345 636645 SUB T 3 345 1 | -369.2 | 1304
498.9738 | 6506.6181 | 1304 | 0.07356 | 636400 HILLS 3 345 636630 SUB 92 3 345 1 | C:636400 HILLS 3 345 636645 SUB T 3 345 1 | -458 | 1304
255.0489 | 3670.1541 | 1439 | 0.04156 | 636400 HILLS 3 345 636645 SUB T 3 345 1 | Base Case | -252.8 | 1439
276.1442 | 3973.715 | 1439 | 0.045 | 636400 HILLS 3 345 636645 SUB T 3 345 1 | C:636620 WALCOTT3 345 636630 SUB 92 3 345 1 | -273.5 | 1439
299.0996 | 4304.0436 | 1439 | 0.04865 | 636400 HILLS 3 345 636645 SUB T 3 345 1 | C:636630 SUB 92 3 345 636640 LOUISA 3 345 1 | -303.7 | 1439
425.3508 | 6120.7975 | 1439 | 0.06924 | 636400 HILLS 3 345 636645 SUB T 3 345 1 | C:636400 HILLS 3 345 636630 SUB 92 3 345 1 | -427.4 | 1439
215.1326 | 5954.8694 | 2768 | -0.07035 | 636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | Base Case | 170.2 | -2768
235.0764 | 6506.9161 | 2768 | -0.07778 | 636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | C:635730 MNTZUMA3 345 636400 HILLS 3 345 1 | 111.3 | -2768
237.2114 | 6566.0122 | 2768 | -0.07697 | 636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | C:631139 HAZLTON3 345 631142 ARNOLD 3 345 1 | 237 | -2768
237.7896 | 6582.0169 | 2768 | -0.07796 | 636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | C:635680 BONDRNT3 345 635730 MNTZUMA3 345 1 | 171.6 | -2768
230.831 | 3395.5242 | 1471 | 0.03297 | 636600 SB 39 3 345 636605 MECCORD3 345 1 | C:636620 WALCOTT3 345 636630 SUB 92 3 345 1 | -684.5 | 1471
267.0822 | 3928.7785 | 1471 | 0.04202 | 636600 SB 39 3 345 636605 MECCORD3 345 1 | C:270866 QUAD 6-7 345 270867 QUAD8-10 345 1 | -473.6 | 1471
307.0144 | 4516.1811 | 1471 | 0.04256 | 636600 SB 39 3 345 636605 MECCORD3 345 1 | C:270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | -1016.6 | 1471
167.6958 | 2003.9653 | 1195 | -0.02064 | 636600 SB 39 3 345 636635 OAKGROV3 345 1 | Base Case | 306.8 | -1195
232.3109 | 2776.1152 | 1195 | -0.03108 | 636600 SB 39 3 345 636635 OAKGROV3 345 1 | C:270866 QUAD 6-7 345 270867 QUAD8-10 345 1 | 220.5 | -1195
255.6476 | 3054.9889 | 1195 | -0.03255 | 636600 SB 39 3 345 636635 OAKGROV3 345 1 | C:636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 378.5 | -1195
258.4509 | 3088.4889 | 1195 | -0.03255 | 636600 SB 39 3 345 636635 OAKGROV3 345 1 | C:636615 SB 56 3 345 636620 WALCOTT3 345 1 | 412 | -1195
247.3427 | 3067.0496 | 1240 | -0.03132 | 636610 SUB 91 3 345 636615 SB 56 3 345 1 | Base Case | 491.7 | -1240
248.5629 | 3082.1801 | 1240 | -0.03304 | 636610 SUB 91 3 345 636615 SB 56 3 345 1 | C:3Wnd: OPEN B$0195 1 | 365.4 | -1240
301.2154 | 3735.0714 | 1240 | -0.0382 | 636610 SUB 91 3 345 636615 SB 56 3 345 1 | C:636600 SB 39 3 345 636635 OAKGROV3 345 1 | 594 | -1240
316.4388 | 3923.8415 | 1240 | -0.04124 | 636610 SUB 91 3 345 636615 SB 56 3 345 1 | C:636635 OAKGROV3 345 636640 LOUISA 3 345 1 | 532.8 | -1240
268.2085 | 3089.7621 | 1152 | -0.03393 | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | Base Case | 299.8 | -1152
302.2864 | 3482.3391 | 1152 | -0.03841 | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 324 | -1152
322.4116 | 3714.1817 | 1152 | -0.04036 | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | C:636600 SB 39 3 345 636635 OAKGROV3 345 1 | 395.5 | -1152
375.8717 | 4330.0418 | 1152 | -0.04829 | 636615 SB 56 3 345 636620 WALCOTT3 345 1 | C:636635 OAKGROV3 345 636640 LOUISA 3 345 1 | 359.3 | -1152
166.7339 | 930.3752 | 558 | 0.01108 | 636615 SB 56 3 345 B$0195 1.00 1 | C:270866 QUAD 6-7 345 636610 SUB 91 3 345 1 | 19.3 | 558
206.3155 | 1151.2407 | 558 | 0.01084 | 636615 SB 56 3 345 B$0195 1.00 1 | C:270866 QUAD 6-7 345 270867 QUAD8-10 345 1 | 259.9 | 558
273.8067 | 1527.8415 | 558 | 0.01798 | 636615 SB 56 3 345 B$0195 1.00 1 | C:636610 SUB 91 3 345 636615 SB 56 3 345 1 | -49.4 | 558
251.8219 | 2994.1621 | 1189 | -0.03393 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | Base Case | 204.2 | -1189
284.8393 | 3386.7391 | 1189 | -0.03841 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 228.4 | -1189
304.3298 | 3618.4817 | 1189 | -0.04036 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | C:636600 SB 39 3 345 636635 OAKGROV3 345 1 | 299.8 | -1189
356.1347 | 4234.4418 | 1189 | -0.04829 | 636620 WALCOTT3 345 636630 SUB 92 3 345 1 | C:636635 OAKGROV3 345 636640 LOUISA 3 345 1 | 263.7 | -1189
174.5172 | 2511.3018 | 1439 | 0.02829 | 636630 SUB 92 3 345 636640 LOUISA 3 345 1 | C:636620 WALCOTT3 345 636630 SUB 92 3 345 1 | -185.1 | 1439
177.554 | 2555.0018 | 1439 | 0.02829 | 636630 SUB 92 3 345 636640 LOUISA 3 345 1 | C:636615 SB 56 3 345 636620 WALCOTT3 345 1 | -228.8 | 1439
224.2905 | 3227.5405 | 1439 | 0.03639 | 636630 SUB 92 3 345 636640 LOUISA 3 345 1 | C:636400 HILLS 3 345 636645 SUB T 3 345 1 | -235.3 | 1439
192.3882 | 2325.9731 | 1209 | -0.02693 | 636635 OAKGROV3 345 636640 LOUISA 3 345 1 | Base Case | 111.6 | -1209
238.4485 | 2882.8424 | 1209 | -0.03446 | 636635 OAKGROV3 345 636640 LOUISA 3 345 1 | C:270866 QUAD 6-7 345 270867 QUAD8-10 345 1 | 49.3 | -1209
312.7458 | 3781.0963 | 1209 | -0.04342 | 636635 OAKGROV3 345 636640 LOUISA 3 345 1 | C:636620 WALCOTT3 345 636630 SUB 92 3 345 1 | 210.8 | -1209
316.5919 | 3827.5963 | 1209 | -0.04342 | 636635 OAKGROV3 345 636640 LOUISA 3 345 1 | C:636615 SB 56 3 345 636620 WALCOTT3 345 1 | 257.3 | -1209
161.025 | 1946.7927 | 1209 | -0.02173 | 636640 LOUISA 3 345 636645 SUB T 3 345 1 | C:636630 SUB 92 3 345 636640 LOUISA 3 345 1 | 160 | -1209
172.6644 | 2087.5122 | 1209 | -0.02349 | 636640 LOUISA 3 345 636645 SUB T 3 345 1 | C:345435 7PALM TAP 345 636645 SUB T 3 345 1 | 156 | -1209
302.471 | 3656.8742 | 1209 | -0.04112 | 636640 LOUISA 3 345 636645 SUB T 3 345 1 | C:636400 HILLS 3 345 636630 SUB 92 3 345 1 | 275.7 | -1209
Entergy
120.2709 | 1046.4769 | 870.1 | -0.01144 | 300040 7FLETCH 345 300047 7SALEM 345 1 | Base Case | -105.8 | -870.1
134.8129 | 1173.0069 | 870.1 | -0.01307 | 300040 7FLETCH 345 300047 7SALEM 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | -98.3 | -870.1
136.3987 | 1186.8047 | 870.1 | -0.01262 | 300040 7FLETCH 345 300047 7SALEM 345 1 | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | -149.1 | -870.1
138.8824 | 1208.4161 | 870.1 | -0.01267 | 300040 7FLETCH 345 300047 7SALEM 345 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | -166.6 | -870.1
112.816 | 981.6118 | 870.1 | 0.01177 | 300040 7FLETCH 345 300054 7GOBKNOB 345 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | 13.8 | 870.1
115.7685 | 1007.3013 | 870.1 | 0.0119 | 300040 7FLETCH 345 300054 7GOBKNOB 345 1 | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 28.8 | 870.1
116.1592 | 1010.7009 | 870.1 | 0.01181 | 300040 7FLETCH 345 300054 7GOBKNOB 345 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | 39.6 | 870.1
247.1433 | 2150.394 | 870.1 | -0.022 | 300041 7FRANKS 345 300042 7HUBEN 345 1 | Base Case | 341.4 | -870.1
255.6029 | 2224.0005 | 870.1 | -0.02335 | 300041 7FRANKS 345 300042 7HUBEN 345 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 304 | -870.1
277.7137 | 2416.3872 | 870.1 | -0.02523 | 300041 7FRANKS 345 300042 7HUBEN 345 1 | C:345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 341.8 | -870.1
279.2588 | 2429.8305 | 870.1 | -0.02498 | 300041 7FRANKS 345 300042 7HUBEN 345 1 | C:345088 7MCCREDIE 345 345230 7MONTGMRY 345 1 | 375.8 | -870.1
128.1418 | 1114.9621 | 870.1 | 0.01067 | 300041 7FRANKS 345 300047 7SALEM 345 1 | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 237.6 | 870.1
130.0399 | 1131.4769 | 870.1 | 0.01144 | 300041 7FRANKS 345 300047 7SALEM 345 1 | C:344154 7BLAND 345 344885 7LABADIE2 345 1 | 190.8 | 870.1
130.2668 | 1133.4512 | 870.1 | 0.01071 | 300041 7FRANKS 345 300047 7SALEM 345 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | 252.8 | 870.1
204.2572 | 1777.2417 | 870.1 | -0.02036 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | C:300045 7MORGAN 345 549984 BROOKLINE 7 345 1 | -103.1 | -870.1
222.6906 | 1937.6306 | 870.1 | -0.02269 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 71.9 | -870.1
227.3513 | 1978.1839 | 870.1 | -0.02222 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | Base Case | 151.1 | -870.1
257.2602 | 2238.4213 | 870.1 | -0.02538 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | C:345408 7OVERTON 345 541201 SIBLEY 7 345 1 | 151.5 | -870.1
217.2566 | 1890.1323 | 870 | -0.01838 | 300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | Base Case | -378.8 | -870
236.1099 | 2054.156 | 870 | -0.01637 | 300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | C:300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | -708.1 | -870
240.2865 | 2090.4929 | 870 | -0.01944 | 300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | C:506935 FLINTCR7 345 512750 TONECE7 345 1 | -492 | -870
245.0261 | 2131.7269 | 870 | -0.01959 | 300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | C:512650 GRDA1 7 345 512750 TONECE7 345 1 | -520.9 | -870
110.9679 | 965.5319 | 870.1 | -0.01133 | 300046 7NEWMAD 345 300051 7STFRANCISTP 345 1 | C:300048 7STFRAN 345 300051 7STFRANCISTP 345 1 | 33.9 | -870.1
117.3154 | 1020.7617 | 870.1 | -0.01058 | 300046 7NEWMAD 345 300051 7STFRANCISTP 345 1 | C:338156 8VINEY 500 338187 8DELL 5 500 1 | -150.8 | -870.1
117.4111 | 1021.5936 | 870.1 | -0.01028 | 300046 7NEWMAD 345 300051 7STFRANCISTP 345 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | -176.3 | -870.1
130.5921 | 1136.282 | 870.1 | -0.01252 | 300051 7STFRANCISTP 345 300054 7GOBKNOB 345 1 | Base Case | 106.8 | -870.1
137.2153 | 1193.9103 | 870.1 | -0.01379 | 300051 7STFRANCISTP 345 300054 7GOBKNOB 345 1 | C:344974 7LUTESVIL 345 345773 7ST FRANC 345 1 | 60 | -870.1
140.9188 | 1226.1343 | 870.1 | -0.01416 | 300051 7STFRANCISTP 345 300054 7GOBKNOB 345 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | 61.8 | -870.1
146.6846 | 1276.3024 | 870.1 | -0.01446 | 300051 7STFRANCISTP 345 300054 7GOBKNOB 345 1 | C:338156 8VINEY 500 338187 8DELL 5 500 1 | 87.3 | -870.1
185.3152 | 1612.2425 | 870 | -0.01587 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | Base Case | -307.3 | -870
204.8831 | 1782.483 | 870 | -0.01737 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | C:300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | -354.2 | -870
206.6572 | 1797.9179 | 870 | -0.0177 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | C:509852 T.NO.--7 345 512650 GRDA1 7 345 1 | -342.5 | -870
209.2483 | 1820.4603 | 870 | -0.01727 | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | C:3Wnd: OPEN B$1237 NEOSHO2X 1 | -400.4 | -870
119.4966 | 1296.5382 | 1085 | -0.01497 | 334028 7GRIMES 345 509241 CROCKET7 345 1 | Base Case | 65.6 | -1085
123.2017 | 1336.7382 | 1085 | -0.01497 | 334028 7GRIMES 345 509241 CROCKET7 345 1 | C:334028 7GRIMES 345 334029 7FRONTR 345 1 | -105.8 | -1085
130.6671 | 1417.7376 | 1085 | -0.01717 | 334028 7GRIMES 345 509241 CROCKET7 345 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | 5.9 | -1085
140.3522 | 1522.8218 | 1085 | -0.01851 | 334028 7GRIMES 345 509241 CROCKET7 345 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | -0.8 | -1085
114.4555 | 1982.3686 | 1732 | 0.02365 | 334325 8HARTBRG 500 335192 8NELSON 500 1 | C:337420 8STERL 500 337561 8ELDEHV 500 1 | 37.7 | 1732
124.4441 | 2155.3711 | 1732 | 0.02419 | 334325 8HARTBRG 500 335192 8NELSON 500 1 | C:336830 8B.WLSN 500 337427 8PERYVIL 500 1 | 166.3 | 1732
215.1044 | 2258.5957 | 1050 | -0.02236 | 334325 8HARTBRG 500 337368 8MTOLIV 500 1 | Base Case | -420 | -1050
230.2489 | 2417.6137 | 1050 | -0.02147 | 334325 8HARTBRG 500 337368 8MTOLIV 500 1 | C:334325 8HARTBRG 500 334370 8COTNWD1 500 1 | -652.2 | -1050
231.8359 | 2434.2772 | 1050 | -0.01849 | 334325 8HARTBRG 500 337368 8MTOLIV 500 1 | C:335368 8WELLS 500 335500 8WEBRE 500 1 | -913.9 | -1050
277.9754 | 2918.7419 | 1050 | -0.0297 | 334325 8HARTBRG 500 337368 8MTOLIV 500 1 | C:336830 8B.WLSN 500 337427 8PERYVIL 500 1 | -476.6 | -1050
109.633 | 1898.8429 | 1732 | -0.01596 | 336130 8BOGALUS 500 336562 8FRKLIN 500 1 | C:335836 8MCKNT 500 336562 8FRKLIN 500 1 | -586.5 | -1732
106.3828 | 2763.825 | 2598 | -0.02152 | 336562 8FRKLIN 500 336820 8G.GULF 500 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | -994.3 | -2598
111.4314 | 2894.9882 | 2598 | -0.02312 | 336562 8FRKLIN 500 336820 8G.GULF 500 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | -993.9 | -2598
150.0969 | 3899.5171 | 2598 | -0.02915 | 336562 8FRKLIN 500 336820 8G.GULF 500 1 | C:336830 8B.WLSN 500 336839 8R.BRAS 500 1 | -1502.6 | -2598
128.8845 | 2232.2792 | 1732 | -0.02123 | 336562 8FRKLIN 500 336839 8R.BRAS 500 1 | C:336562 8FRKLIN 500 336820 8G.GULF 500 1 | -486.6 | -1732
107.5956 | 2795.3342 | 2598 | 0.02112 | 336830 8B.WLSN 500 336839 8R.BRAS 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 1058.7 | 2598
119.8175 | 3112.8593 | 2598 | 0.03101 | 336830 8B.WLSN 500 336839 8R.BRAS 500 1 | C:336820 8G.GULF 500 336830 8B.WLSN 500 1 | 563 | 2598
160.6027 | 4172.4593 | 2598 | 0.03101 | 336830 8B.WLSN 500 336839 8R.BRAS 500 1 | C:336562 8FRKLIN 500 336820 8G.GULF 500 1 | 1622.6 | 2598
185.8131 | 3218.2821 | 1732 | -0.03578 | 336830 8B.WLSN 500 337427 8PERYVIL 500 1 | Base Case | -276.2 | -1732
212.708 | 3684.1023 | 1732 | -0.04001 | 336830 8B.WLSN 500 337427 8PERYVIL 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | -394.2 | -1732
218.7405 | 3788.5847 | 1732 | -0.04099 | 336830 8B.WLSN 500 337427 8PERYVIL 500 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | -418.1 | -1732
230.139 | 3986.0073 | 1732 | -0.04338 | 336830 8B.WLSN 500 337427 8PERYVIL 500 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | -419 | -1732
145.5478 | 2520.8878 | 1732 | -0.02303 | 337368 8MTOLIV 500 337561 8ELDEHV 500 1 | Base Case | -627.2 | -1732
155.3921 | 2691.392 | 1732 | -0.01926 | 337368 8MTOLIV 500 337561 8ELDEHV 500 1 | C:335368 8WELLS 500 335500 8WEBRE 500 1 | -1107.7 | -1732
182.6264 | 3163.0886 | 1732 | -0.03017 | 337368 8MTOLIV 500 337561 8ELDEHV 500 1 | C:336830 8B.WLSN 500 337427 8PERYVIL 500 1 | -682.3 | -1732
196.3319 | 3400.4686 | 1732 | -0.03528 | 337368 8MTOLIV 500 337561 8ELDEHV 500 1 | C:337420 8STERL 500 337561 8ELDEHV 500 1 | -499.5 | -1732
243.0892 | 2178.079 | 896 | 0.01885 | 337376 7SAREPT 345 337562 7ELDEHV 345 1 | C:334028 7GRIMES 345 509241 CROCKET7 345 1 | -628.1 | 896
247.8277 | 2220.5361 | 896 | 0.01919 | 337376 7SAREPT 345 337562 7ELDEHV 345 1 | C:500250 DOLHILL7 345 507760 SW SHV 7 345 1 | -642.6 | 896
250.8513 | 2247.6278 | 896 | -0.01977 | 337376 7SAREPT 345 508809 LONGWD 7 345 1 | Base Case | 622 | -896
272.9957 | 2446.0415 | 896 | -0.02265 | 337376 7SAREPT 345 508809 LONGWD 7 345 1 | C:337808 8MABEL 500 337909 8ANO 50 500 1 | 583.6 | -896
291.8382 | 2614.8703 | 896 | -0.02401 | 337376 7SAREPT 345 508809 LONGWD 7 345 1 | C:334028 7GRIMES 345 509241 CROCKET7 345 1 | 640.6 | -896
308.6619 | 2765.6108 | 896 | -0.02551 | 337376 7SAREPT 345 508809 LONGWD 7 345 1 | C:500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 668 | -896
202.8909 | 3514.0701 | 1732 | -0.03793 | 337420 8STERL 500 337561 8ELDEHV 500 1 | Base Case | 395.2 | -1732
217.4899 | 3766.9257 | 1732 | -0.04258 | 337420 8STERL 500 337561 8ELDEHV 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 265.7 | -1732
231.5292 | 4010.0852 | 1732 | -0.04575 | 337420 8STERL 500 337561 8ELDEHV 500 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | 248.2 | -1732
233.8199 | 4049.7611 | 1732 | -0.04767 | 337420 8STERL 500 337561 8ELDEHV 500 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | 130 | -1732
225.9838 | 3914.0401 | 1732 | 0.0363 | 337515 8MCNEIL 500 337561 8ELDEHV 500 1 | C:337561 8ELDEHV 500 337643 8SHERID 500 1 | -929.2 | 1732
243.1673 | 2178.7789 | 896 | -0.01885 | 337561 8ELDEHV 500 337562 7ELDEHV 345 1 | C:334028 7GRIMES 345 509241 CROCKET7 345 1 | 628.8 | -896
247.9058 | 2221.2361 | 896 | -0.01919 | 337561 8ELDEHV 500 337562 7ELDEHV 345 1 | C:500250 DOLHILL7 345 507760 SW SHV 7 345 1 | 643.3 | -896
212.7788 | 3685.3287 | 1732 | -0.03625 | 337561 8ELDEHV 500 337643 8SHERID 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 704.6 | -1732
247.3334 | 4283.8149 | 1732 | -0.04033 | 337561 8ELDEHV 500 337643 8SHERID 500 1 | C:337515 8MCNEIL 500 337754 8ETTA 500 1 | 967.6 | -1732
264.3085 | 4577.8235 | 1732 | -0.04213 | 337561 8ELDEHV 500 337643 8SHERID 500 1 | C:337515 8MCNEIL 500 337561 8ELDEHV 500 1 | 1113.6 | -1732
125.856 | 2179.8253 | 1732 | 0.01227 | 337643 8SHERID 500 337651 8WH BLF 500 1 | C:336830 8B.WLSN 500 337427 8PERYVIL 500 1 | 1170.9 | 1732
277.8677 | 4812.6684 | 1732 | 0.03757 | 337643 8SHERID 500 337651 8WH BLF 500 1 | C:337808 8MABEL 500 337860 8KNWRIVL 500 1 | 1723.4 | 1732
290.8704 | 5037.8759 | 1732 | 0.03681 | 337643 8SHERID 500 337651 8WH BLF 500 1 | C:337860 8KNWRIVL 500 337957 8KEO 500 1 | 2011.1 | 1732
263.8016 | 4569.0431 | 1732 | -0.04856 | 337643 8SHERID 500 337808 8MABEL 500 1 | Base Case | 576.1 | -1732
272.5232 | 4720.1014 | 1732 | -0.05146 | 337643 8SHERID 500 337808 8MABEL 500 1 | C:508298 LYDIA 7 345 508359 WELSH 7 345 1 | 488.7 | -1732
390.0905 | 6756.3673 | 1732 | -0.08153 | 337643 8SHERID 500 337808 8MABEL 500 1 | C:337808 8MABEL 500 337860 8KNWRIVL 500 1 | -52.4 | -1732
400.0356 | 6928.6163 | 1732 | -0.08016 | 337643 8SHERID 500 337808 8MABEL 500 1 | C:337860 8KNWRIVL 500 337957 8KEO 500 1 | -337.3 | -1732
215.1966 | 4659.0073 | 2165 | 0.03642 | 337651 8WH BLF 500 337957 8KEO 500 1 | C:337808 8MABEL 500 337860 8KNWRIVL 500 1 | 1664.3 | 2165
238.3907 | 5161.1596 | 2165 | 0.03806 | 337651 8WH BLF 500 337957 8KEO 500 1 | C:337860 8KNWRIVL 500 337957 8KEO 500 1 | 2031.6 | 2165
276.9197 | 4796.2485 | 1732 | 0.04735 | 337808 8MABEL 500 337860 8KNWRIVL 500 1 | Base Case | 902.8 | 1732
287.0963 | 4972.5073 | 1732 | 0.04805 | 337808 8MABEL 500 337860 8KNWRIVL 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1021.5 | 1732
335.964 | 5818.8958 | 1732 | 0.05029 | 337808 8MABEL 500 337860 8KNWRIVL 500 1 | C:337651 8WH BLF 500 337957 8KEO 500 1 | 1683.7 | 1732
345.3023 | 5980.6363 | 1732 | 0.05179 | 337808 8MABEL 500 337860 8KNWRIVL 500 1 | C:337643 8SHERID 500 337651 8WH BLF 500 1 | 1722.1 | 1732
291.2912 | 5045.1633 | 1732 | -0.05279 | 337808 8MABEL 500 337909 8ANO 50 500 1 | Base Case | -704.4 | -1732
393.2593 | 6811.2517 | 1732 | -0.07362 | 337808 8MABEL 500 337909 8ANO 50 500 1 | C:337808 8MABEL 500 337937 8MAYFL 500 1 | -757.7 | -1732
445.8061 | 7721.3621 | 1732 | -0.08045 | 337808 8MABEL 500 337909 8ANO 50 500 1 | C:337922 8P HILL 500 337937 8MAYFL 500 1 | -1106.2 | -1732
468.2926 | 8110.8279 | 1732 | -0.08259 | 337808 8MABEL 500 337909 8ANO 50 500 1 | C:337909 8ANO 50 500 337922 8P HILL 500 1 | -1319.7 | -1732
220.2895 | 3815.415 | 1732 | -0.045 | 337808 8MABEL 500 337937 8MAYFL 500 1 | Base Case | -115.2 | -1732
227.1283 | 3933.8617 | 1732 | -0.04547 | 337808 8MABEL 500 337937 8MAYFL 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -195 | -1732
231.269 | 4005.5786 | 1732 | -0.04669 | 337808 8MABEL 500 337937 8MAYFL 500 1 | C:508298 LYDIA 7 345 508359 WELSH 7 345 1 | -166.4 | -1732
395.043 | 6842.1441 | 1732 | -0.07667 | 337808 8MABEL 500 337937 8MAYFL 500 1 | C:337808 8MABEL 500 337909 8ANO 50 500 1 | -537.8 | -1732
235.2167 | 5092.4411 | 2165 | 0.04582 | 337860 8KNWRIVL 500 337957 8KEO 500 1 | Base Case | 1324.8 | 2165
243.4375 | 5270.4223 | 2165 | 0.04653 | 337860 8KNWRIVL 500 337957 8KEO 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1444.4 | 2165
285.8974 | 6189.6785 | 2165 | 0.04898 | 337860 8KNWRIVL 500 337957 8KEO 500 1 | C:337651 8WH BLF 500 337957 8KEO 500 1 | 2162.2 | 2165
289.7324 | 6272.7068 | 2165 | 0.05025 | 337860 8KNWRIVL 500 337957 8KEO 500 1 | C:337643 8SHERID 500 337651 8WH BLF 500 1 | 2140.8 | 2165
323.0199 | 5594.7043 | 1732 | 0.05438 | 337909 8ANO 50 500 337922 8P HILL 500 1 | Base Case | 1123.2 | 1732
332.5331 | 5759.4741 | 1732 | 0.05504 | 337909 8ANO 50 500 337922 8P HILL 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1233.7 | 1732
346.1877 | 5995.9718 | 1732 | 0.05688 | 337909 8ANO 50 500 337922 8P HILL 500 1 | C:3Wnd: OPEN B$0371 ANO 1 | 1318.9 | 1732
509.957 | 8832.455 | 1732 | 0.08826 | 337909 8ANO 50 500 337922 8P HILL 500 1 | C:337808 8MABEL 500 337909 8ANO 50 500 1 | 1575.1 | 1732
261.8308 | 3401.1817 | 1299 | -0.04036 | 337909 8ANO 50 500 515305 FTSMITH8 500 1 | Base Case | -82.5 | -1299
270.5299 | 3514.1839 | 1299 | -0.04081 | 337909 8ANO 50 500 515305 FTSMITH8 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -158.5 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 1 | C:337909 8ANO 50 500 515305 FTSMITH8 500 3 | -114.8 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 1 | C:337909 8ANO 50 500 515305 FTSMITH8 500 2 | -114.8 | -1299
261.8308 | 3401.1817 | 1299 | -0.04036 | 337909 8ANO 50 500 515305 FTSMITH8 500 2 | Base Case | -82.5 | -1299
270.5299 | 3514.1839 | 1299 | -0.04081 | 337909 8ANO 50 500 515305 FTSMITH8 500 2 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -158.5 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 2 | C:337909 8ANO 50 500 515305 FTSMITH8 500 3 | -114.8 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 2 | C:337909 8ANO 50 500 515305 FTSMITH8 500 1 | -114.8 | -1299
261.8308 | 3401.1817 | 1299 | -0.04036 | 337909 8ANO 50 500 515305 FTSMITH8 500 3 | Base Case | -82.5 | -1299
270.5299 | 3514.1839 | 1299 | -0.04081 | 337909 8ANO 50 500 515305 FTSMITH8 500 3 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -158.5 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 3 | C:337909 8ANO 50 500 515305 FTSMITH8 500 2 | -114.8 | -1299
364.2684 | 4731.8461 | 1299 | -0.05615 | 337909 8ANO 50 500 515305 FTSMITH8 500 3 | C:337909 8ANO 50 500 515305 FTSMITH8 500 1 | -114.8 | -1299
258.5402 | 1737.3902 | 672 | 0.01423 | 337909 8ANO 50 500 B$0371 ANO 1.00 1 | C:337909 8ANO 50 500 337922 8P HILL 500 1 | 567.3 | 672
285.3496 | 4942.2552 | 1732 | 0.05108 | 337922 8P HILL 500 337937 8MAYFL 500 1 | Base Case | 742.1 | 1732
293.61 | 5085.3246 | 1732 | 0.05165 | 337922 8P HILL 500 337937 8MAYFL 500 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 838.3 | 1732
297.0302 | 5144.5638 | 1732 | 0.05288 | 337922 8P HILL 500 337937 8MAYFL 500 1 | C:508298 LYDIA 7 345 508359 WELSH 7 345 1 | 796.4 | 1732
464.8973 | 8052.0217 | 1732 | 0.08362 | 337922 8P HILL 500 337937 8MAYFL 500 1 | C:337808 8MABEL 500 337909 8ANO 50 500 1 | 1176.2 | 1732
157.0412 | 2719.9534 | 1732 | 0.01583 | 337957 8KEO 500 338140 8HOLBT 500 1 | Base Case | 1418.3 | 1732
216.7226 | 3753.636 | 1732 | 0.02615 | 337957 8KEO 500 338140 8HOLBT 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 1603.4 | 1732
217.7503 | 3771.4361 | 1732 | 0.02615 | 337957 8KEO 500 338140 8HOLBT 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 1621.2 | 1732
251.5455 | 4356.7689 | 1732 | 0.0307 | 337957 8KEO 500 338140 8HOLBT 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 1832.4 | 1732
215.6919 | 3735.7844 | 1732 | 0.03394 | 337957 8KEO 500 338162 8WM-EHV 500 1 | Base Case | 945 | 1732
260.3686 | 4509.5847 | 1732 | 0.04099 | 337957 8KEO 500 338162 8WM-EHV 500 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | 1139.1 | 1732
263.5172 | 4564.1185 | 1732 | 0.03876 | 337957 8KEO 500 338162 8WM-EHV 500 1 | C:337957 8KEO 500 338140 8HOLBT 500 1 | 1377 | 1732
281.8985 | 4882.4816 | 1732 | 0.04265 | 337957 8KEO 500 338162 8WM-EHV 500 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | 1375.5 | 1732
172.7193 | 2991.4974 | 1732 | 0.02272 | 338140 8HOLBT 500 338145 8ISES 500 1 | Base Case | 1123.3 | 1732
227.0861 | 3933.1312 | 1732 | 0.03212 | 338140 8HOLBT 500 338145 8ISES 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 1292 | 1732
228.0214 | 3949.3312 | 1732 | 0.03212 | 338140 8HOLBT 500 338145 8ISES 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 1308.2 | 1732
258.6378 | 4479.6065 | 1732 | 0.03624 | 338140 8HOLBT 500 338145 8ISES 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 1499.7 | 1732
150.6846 | 2609.8581 | 1732 | 0.02378 | 338145 8ISES 500 338156 8VINEY 500 1 | Base Case | 654.5 | 1732
209.3268 | 3625.5398 | 1732 | 0.03392 | 338145 8ISES 500 338156 8VINEY 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 836.4 | 1732
210.3372 | 3643.0398 | 1732 | 0.03392 | 338145 8ISES 500 338156 8VINEY 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 853.9 | 1732
222.425 | 3852.4009 | 1732 | 0.03507 | 338145 8ISES 500 338156 8VINEY 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 968.7 | 1732
134.6394 | 2331.954 | 1732 | 0.02526 | 338156 8VINEY 500 338187 8DELL 5 500 1 | Base Case | 254.9 | 1732
199.5909 | 3456.914 | 1732 | 0.03548 | 338156 8VINEY 500 338187 8DELL 5 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 539.5 | 1732
210.4475 | 3644.95 | 1732 | 0.03837 | 338156 8VINEY 500 338187 8DELL 5 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 489.9 | 1732
211.7523 | 3667.55 | 1732 | 0.03837 | 338156 8VINEY 500 338187 8DELL 5 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 512.5 | 1732
214.5276 | 3715.6187 | 1732 | 0.03647 | 338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | Base Case | 716.8 | 1732
250.344 | 4335.9582 | 1732 | 0.04008 | 338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | C:337957 8KEO 500 338140 8HOLBT 500 1 | 1040.3 | 1732
257.8725 | 4466.3514 | 1732 | 0.04331 | 338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | 905.1 | 1732
264.1952 | 4575.861 | 1732 | 0.043 | 338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | 1040.1 | 1732
137.4482 | 3570.904 | 2598 | 0.04037 | 338187 8DELL 5 500 338188 8SANSOUCI 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 251.4 | 2598
151.7088 | 3941.394 | 2598 | 0.04526 | 338187 8DELL 5 500 338188 8SANSOUCI 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 219.8 | 2598
152.8289 | 3970.494 | 2598 | 0.04526 | 338187 8DELL 5 500 338188 8SANSOUCI 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 248.9 | 2598
138.672 | 3570.804 | 2575 | 0.04037 | 338188 8SANSOUCI 500 360021 8SHELBY TN 500 1 | C:337957 8KEO 500 338162 8WM-EHV 500 1 | 251.3 | 2575
153.06 | 3941.294 | 2575 | 0.04526 | 338188 8SANSOUCI 500 360021 8SHELBY TN 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 219.7 | 2575
154.1939 | 3970.494 | 2575 | 0.04526 | 338188 8SANSOUCI 500 360021 8SHELBY TN 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 248.9 | 2575
TVA
106.5278 | 1473.28 | 1383 | -0.01674 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 1 | Base Case | -96.8 | -1383
120.7891 | 1670.5139 | 1383 | -0.01918 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 1 | C:347830 7NEWTON 345 348493 7XENIA 345 1 | -93.4 | -1383
126.987 | 1756.2304 | 1383 | -0.02031 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 1 | C:338187 8DELL 5 500 338188 8SANSOUCI 500 1 | -86.2 | -1383
126.987 | 1756.2304 | 1383 | -0.02031 | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 1 | C:338188 8SANSOUCI 500 360021 8SHELBY TN 500 1 | -86.2 | -1383
100.1076 | 2600.8947 | 2598.1 | -0.02447 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | C:360019 8JACKSON TN 500 360037 8JVILLE FP 500 1 | -588.8 | -2598.1
110.6171 | 2873.944 | 2598.1 | -0.02548 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | C:360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | -778.8 | -2598.1
110.6287 | 2874.244 | 2598.1 | -0.02548 | 360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | C:360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | -779.1 | -2598.1
117.7524 | 2495.4087 | 2119.2 | 0.02973 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | C:360019 8JACKSON TN 500 360037 8JVILLE FP 500 1 | 50.8 | 2119.2
120.2256 | 2547.822 | 2119.2 | 0.02785 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | C:360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | 257.8 | 2119.2
120.2398 | 2548.1219 | 2119.2 | 0.02785 | 360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | C:360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | 258.1 | 2119.2
105.8172 | 2268.0848 | 2143.4 | -0.0224 | 360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | Base Case | -426.2 | -2143.4
134.4632 | 2882.0847 | 2143.4 | -0.02936 | 360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | C:360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | -467.9 | -2143.4
134.4632 | 2882.0847 | 2143.4 | -0.02936 | 360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | C:360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | -467.9 | -2143.4
142.9404 | 3063.7839 | 2143.4 | -0.02918 | 360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | C:360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | -664.4 | -2143.4
114.831 | 1988.9878 | 1732.1 | 0.02303 | 360021 8SHELBY TN 500 360025 8CORDOVA TN 500 1 | C:360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | 95.3 | 1732.1
116.309 | 2014.5878 | 1732.1 | 0.02303 | 360021 8SHELBY TN 500 360025 8CORDOVA TN 500 1 | C:338162 8WM-EHV 500 360075 8BHAM STEEL 500 1 | 120.9 | 1732.1
164.106 | 2842.4793 | 1732.1 | 0.0259 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | Base Case | 712.8 | 1732.1
192.1934 | 3328.9817 | 1732.1 | 0.02873 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | C:337957 8KEO 500 338140 8HOLBT 500 1 | 966.6 | 1732.1
201.9499 | 3497.9745 | 1732.1 | 0.03187 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | 877.4 | 1732.1
205.5434 | 3560.2165 | 1732.1 | 0.03135 | 360023 8FREEPORT TN 500 360025 8CORDOVA TN 500 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | 982.4 | 1732.1
172.3678 | 3652.8187 | 2119.2 | -0.03647 | 360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | Base Case | -654 | -2119.2
201.6402 | 4273.1582 | 2119.2 | -0.04008 | 360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | C:337957 8KEO 500 338140 8HOLBT 500 1 | -977.5 | -2119.2
207.7884 | 4403.4514 | 2119.2 | -0.04331 | 360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | C:338145 8ISES 500 338156 8VINEY 500 1 | -842.2 | -2119.2
212.9559 | 4512.961 | 2119.2 | -0.043 | 360023 8FREEPORT TN 500 360075 8BHAM STEEL 500 1 | C:338140 8HOLBT 500 338145 8ISES 500 1 | -977.2 | -2119.2
131.0077 | 2269.1848 | 1732.1 | 0.0224 | 360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | Base Case | 427.3 | 1732.1
166.4502 | 2883.0847 | 1732.1 | 0.02936 | 360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | C:360017 8WEAKLEY TN 500 360582 8GLEASON CT 500 1 | 468.9 | 1732.1
166.4502 | 2883.0847 | 1732.1 | 0.02936 | 360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | C:360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | 468.9 | 1732.1
176.9404 | 3064.7839 | 1732.1 | 0.02918 | 360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | C:360017 8WEAKLEY TN 500 360568 8LAG CRK CT 500 1 | 665.4 | 1732.1
121.7217 | 3162.4519 | 2598.1 | 0.03644 | 360037 8JVILLE FP 500 360040 8CUMBERLAND 500 1 | C:360037 8JVILLE FP 500 360048 8DAVIDSON TN 500 1 | -166.1 | 2598.1
109.99 | 2857.649 | 2598.1 | 0.03352 | 360037 8JVILLE FP 500 360048 8DAVIDSON TN 500 1 | C:360037 8JVILLE FP 500 360040 8CUMBERLAND 500 1 | 101.4 | 2598.1
117.7524 | 2495.4087 | 2119.2 | -0.02973 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | C:360019 8JACKSON TN 500 360037 8JVILLE FP 500 1 | -50.8 | -2119.2
120.2256 | 2547.822 | 2119.2 | -0.02785 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | C:360019 8JACKSON TN 500 360542 8HAYWOOD TN 500 1 | -257.8 | -2119.2
120.2398 | 2548.1219 | 2119.2 | -0.02785 | 360037 8JVILLE FP 500 360582 8GLEASON CT 500 1 | C:360025 8CORDOVA TN 500 360542 8HAYWOOD TN 500 1 | -258.1 | -2119.2
109.5485 | 1897.4891 | 1732.1 | 0.01167 | 360044 8MONTGOMERY 500 360071 8WILSON TN 500 1 | C:360048 8DAVIDSON TN 500 360581 8PIN HOOK TN 500 1 | 937.9 | 1732.1
112.2666 | 2916.7991 | 2598.1 | -0.01841 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | Base Case | -1403 | -2598.1
125.3453 | 3256.5967 | 2598.1 | -0.01558 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | C:360042 8PARADISE FP 500 360044 8MONTGOMERY 500 1 | -1975.5 | -2598.1
140.4715 | 3649.5891 | 2598.1 | -0.0233 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | C:360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | -1733.7 | -2598.1
144.5438 | 3755.3913 | 2598.1 | -0.02842 | 360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | C:360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | -1418.5 | -2598.1
109.5778 | 2846.9405 | 2598.1 | 0.02476 | 360052 8BR FERRY NP 500 360060 8MADISON AL 500 1 | C:360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 811 | 2598.1
128.1478 | 3329.4073 | 2598.1 | 0.03175 | 360052 8BR FERRY NP 500 360060 8MADISON AL 500 1 | C:360060 8MADISON AL 500 360088 8LIMESTONE 500 1 | 718.7 | 2598.1
146.4045 | 3803.7345 | 2598.1 | 0.03513 | 360052 8BR FERRY NP 500 360060 8MADISON AL 500 1 | C:360052 8BR FERRY NP 500 360088 8LIMESTONE 500 1 | 915.1 | 2598.1
105.7951 | 2748.6621 | 2598.1 | 0.0223 | 360052 8BR FERRY NP 500 360088 8LIMESTONE 500 1 | C:306101 8BAD CRK 500 306102 8JOCASSE 500 1 | 915 | 2598.1
122.4662 | 3181.7945 | 2598.1 | 0.02676 | 360052 8BR FERRY NP 500 360088 8LIMESTONE 500 1 | C:360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 981.4 | 2598.1
155.236 | 4033.1877 | 2598.1 | 0.03695 | 360052 8BR FERRY NP 500 360088 8LIMESTONE 500 1 | C:360052 8BR FERRY NP 500 360060 8MADISON AL 500 1 | 994.9 | 2598.1
107.7327 | 2799.0041 | 2598.1 | 0.03341 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | Base Case | 51.8 | 2598.1
124.5065 | 3234.8041 | 2598.1 | 0.03341 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | C:360065 8WID CRK FP 500 360079 8RACCOON MTN 500 1 | 487.6 | 2598.1
124.5758 | 3236.6041 | 2598.1 | 0.03341 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | C:306101 8BAD CRK 500 306102 8JOCASSE 500 1 | 489.4 | 2598.1
148.2781 | 3852.4136 | 2598.1 | 0.04006 | 360060 8MADISON AL 500 360062 8BELLEF NP1 500 1 | C:360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 558.4 | 2598.1
125.6852 | 3265.4278 | 2598.1 | -0.0314 | 360060 8MADISON AL 500 360088 8LIMESTONE 500 1 | C:360052 8BR FERRY NP 500 360060 8MADISON AL 500 1 | -683.5 | -2598.1
121.1417 | 3147.3819 | 2598.1 | 0.03807 | 360062 8BELLEF NP1 500 360063 8BELLEF NP2 500 1 | C:360062 8BELLEF NP1 500 360065 8WID CRK FP 500 1 | 17 | 2598.1
110.4552 | 2869.7373 | 2598.1 | 0.03338 | 360062 8BELLEF NP1 500 360065 8WID CRK FP 500 1 | C:360062 8BELLEF NP1 500 360063 8BELLEF NP2 500 1 | 125 | 2598.1
117.0067 | 3039.9517 | 2598.1 | 0.0271 | 360062 8BELLEF NP1 500 360065 8WID CRK FP 500 1 | C:360063 8BELLEF NP2 500 360065 8WID CRK FP 500 1 | 811.6 | 2598.1
107.6787 | 2281.928 | 2119.2 | 0.01748 | 360063 8BELLEF NP2 500 360065 8WID CRK FP 500 1 | C:360065 8WID CRK FP 500 360079 8RACCOON MTN 500 1 | 844.6 | 2119.2
120.9938 | 2564.1015 | 2119.2 | 0.02124 | 360063 8BELLEF NP2 500 360065 8WID CRK FP 500 1 | C:360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 817.6 | 2119.2
151.1825 | 3203.8586 | 2119.2 | 0.02854 | 360063 8BELLEF NP2 500 360065 8WID CRK FP 500 1 | C:360062 8BELLEF NP1 500 360065 8WID CRK FP 500 1 | 857.1 | 2119.2
188.7332 | 3269.0486 | 1732.1 | 0.0218 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | Base Case | 1476.5 | 1732.1
197.4275 | 3419.6426 | 1732.1 | 0.02054 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | C:360042 8PARADISE FP 500 360044 8MONTGOMERY 500 1 | 1730.7 | 1732.1
205.2508 | 3555.1486 | 1732.1 | 0.0218 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | C:306101 8BAD CRK 500 306102 8JOCASSE 500 1 | 1762.6 | 1732.1
237.5695 | 4114.9408 | 1732.1 | 0.02714 | 360065 8WID CRK FP 500 360081 8SEQUOYAH NP 500 1 | C:360050 8MAURY TN 500 360052 8BR FERRY NP 500 1 | 1883.3 | 1732.1
134.6071 | 3497.2269 | 2598.1 | 0.01959 | 360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 | Base Case | 1886.4 | 2598.1
145.0224 | 3767.8269 | 2598.1 | 0.01959 | 360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 | C:306101 8BAD CRK 500 306102 8JOCASSE 500 1 | 2157 | 2598.1
146.1784 | 3797.8623 | 2598.1 | 0.02001 | 360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 | C:383021 8LONGLEAF 500 384600 8FARLEY 8 500 1 | 2152.5 | 2598.1
148.013 | 3845.5269 | 2598.1 | 0.01959 | 360081 8SEQUOYAH NP 500 360662 8BRADLEY TN 500 1 | C:380023 8WANSLEY 500 382496 8WANSLEY 6&7 500 1 | 2234.7 | 2598.1
103.3927 | 2686.2462 | 2598.1 | 0.01897 | 360090 8ROANE TN 500 360093 8BULL RUN FP 500 1 | C:360085 8WBNP #1 500 360093 8BULL RUN FP 500 1 | 1126.4 | 2598.1
105.6296 | 2744.3623 | 2598.1 | 0.02001 | 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1 | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | 1099 | 2598.1
105.6681 | 2745.3623 | 2598.1 | 0.02001 | 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1 | C:382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | 1100 | 2598.1
126.633 | 3290.0512 | 2598.1 | 0.02234 | 360093 8BULL RUN FP 500 360097 8VOLUNTEER 500 1 | C:360085 8WBNP #1 500 360097 8VOLUNTEER 500 1 | 1453.1 | 2598.1
107.46 | 2791.9193 | 2598.1 | 0.02264 | 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1 | C:360662 8BRADLEY TN 500 383045 8CONASAUG CC 500 1 | 930.3 | 2598.1
110.8298 | 2879.469 | 2598.1 | 0.02374 | 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1 | C:380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | 927.4 | 2598.1
110.8837 | 2880.869 | 2598.1 | 0.02374 | 360097 8VOLUNTEER 500 360102 8PHIPPS B NP 500 1 | C:382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | 928.8 | 2598.1
136.4143 | 3544.0434 | 2598 | 0.02072 | 360662 8BRADLEY TN 500 383045 8CONASAUG CC 500 1 | Base Case | 1840.3 | 2598
148.8008 | 3865.8456 | 2598 | 0.02117 | 360662 8BRADLEY TN 500 383045 8CONASAUG CC 500 1 | C:382500 8RACCOON CK 500 383021 8LONGLEAF 500 1 | 2125.1 | 2598
149.0087 | 3871.2456 | 2598 | 0.02117 | 360662 8BRADLEY TN 500 383045 8CONASAUG CC 500 1 | C:383021 8LONGLEAF 500 384600 8FARLEY 8 500 1 | 2130.5 | 2598
150.8485 | 3919.0434 | 2598 | 0.02072 | 360662 8BRADLEY TN 500 383045 8CONASAUG CC 500 1 | C:380023 8WANSLEY 500 382496 8WANSLEY 6&7 500 1 | 2215.3 | 2598
SOCO
112.1171 | 3844.4954 | 3429 | -0.02694 | 380020 8BOWEN 500 380021 8MOSTELLER 500 1 | C:380021 8MOSTELLER 500 380025 8MCGRAU FORD 500 1 | -1629.3 | -3429
120.8467 | 4143.835 | 3429 | -0.02826 | 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | Base Case | -1820.1 | -3429
130.2584 | 4466.5594 | 3429 | -0.02872 | 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | C:382500 8RACCOON CK 500 383021 8LONGLEAF 500 1 | -2105 | -3429
130.4129 | 4471.8594 | 3429 | -0.02872 | 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | C:383021 8LONGLEAF 500 384600 8FARLEY 8 500 1 | -2110.3 | -3429
131.7829 | 4518.835 | 3429 | -0.02826 | 380021 8MOSTELLER 500 382499 8CONASAUGA 500 1 | C:380023 8WANSLEY 500 382496 8WANSLEY 6&7 500 1 | -2195.1 | -3429
157.6015 | 4094.4869 | 2598 | -0.02285 | 382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | C:306105 8OCONEE 500 380006 8MIDDLE FORK 500 1 | -2215.6 | -2598
159.8628 | 4153.235 | 2598 | -0.02826 | 382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | Base Case | -1829.5 | -2598
172.4888 | 4481.2594 | 2598 | -0.02872 | 382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | C:383021 8LONGLEAF 500 384600 8FARLEY 8 500 1 | -2119.7 | -2598
174.297 | 4528.235 | 2598 | -0.02826 | 382499 8CONASAUGA 500 383045 8CONASAUG CC 500 1 | C:380023 8WANSLEY 500 382496 8WANSLEY 6&7 500 1 | -2204.5 | -2598
SPP
133.2289 | 1580.0948 | 1186 | -0.01751 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | Base Case | 140.3 | -1186
144.073 | 1708.706 | 1186 | -0.01985 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | 76.5 | -1186
153.601 | 1821.7081 | 1186 | -0.0203 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | C:334028 7GRIMES 345 509241 CROCKET7 345 1 | 152.5 | -1186
173.6925 | 2059.9927 | 1186 | -0.02173 | 500250 DOLHILL7 345 507760 SW SHV 7 345 1 | C:337376 7SAREPT 345 508809 LONGWD 7 345 1 | 273.2 | -1186
150.7913 | 1801.9555 | 1195 | -0.01161 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | C:300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | -847.3 | -1195
108.3308 | 1224.1384 | 1130 | 0.01268 | 506935 FLINTCR7 345 547481 MON383 7 345 1 | C:300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | 181.5 | 1130
119.2657 | 1402.5642 | 1176 | -0.01112 | 507760 SW SHV 7 345 508809 LONGWD 7 345 1 | C:507760 SW SHV 7 345 508832 DIANA 7 345 1 | -488.2 | -1176
119.9381 | 1270.1439 | 1059 | -0.01385 | 507760 SW SHV 7 345 508832 DIANA 7 345 1 | Base Case | -131.3 | -1059
153.5205 | 1625.7817 | 1059 | -0.0171 | 507760 SW SHV 7 345 508832 DIANA 7 345 1 | C:508563 PIRKEY 7 345 508832 DIANA 7 345 1 | -219.7 | -1059
168.5888 | 1785.3558 | 1059 | -0.01866 | 507760 SW SHV 7 345 508832 DIANA 7 345 1 | C:508359 WELSH 7 345 508841 WILKES 7 345 1 | -251 | -1059
187.1665 | 1982.0931 | 1059 | -0.02182 | 507760 SW SHV 7 345 508832 DIANA 7 345 1 | C:508809 LONGWD 7 345 508841 WILKES 7 345 1 | -187.9 | -1059
191.43 | 2027.2435 | 1059 | 0.01376 | 508072 NWTXARK7 345 508298 LYDIA 7 345 1 | Base Case | 895.8 | 1059
211.3502 | 2238.199 | 1059 | 0.01374 | 508072 NWTXARK7 345 508298 LYDIA 7 345 1 | C:508072 NWTXARK7 345 510911 VALIANT7 345 1 | 1108.4 | 1059
215.1571 | 2278.5133 | 1059 | 0.01442 | 508072 NWTXARK7 345 508298 LYDIA 7 345 1 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | 1092.8 | 1059
300.7952 | 3185.421 | 1059 | 0.023 | 508072 NWTXARK7 345 508298 LYDIA 7 345 1 | C:508072 NWTXARK7 345 508359 WELSH 7 345 1 | 1294.2 | 1059
232.7094 | 2464.3926 | 1059 | 0.01706 | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | C:337376 7SAREPT 345 508809 LONGWD 7 345 1 | 1061.6 | 1059
253.6567 | 2686.2246 | 1059 | 0.02143 | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | Base Case | 924.1 | 1059
314.8653 | 3334.4234 | 1059 | 0.02583 | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | C:508072 NWTXARK7 345 508298 LYDIA 7 345 1 | 1210.5 | 1059
415.1954 | 4396.9196 | 1059 | 0.03665 | 508072 NWTXARK7 345 508359 WELSH 7 345 1 | C:508298 LYDIA 7 345 508359 WELSH 7 345 1 | 1383.3 | 1059
108.0026 | 2989.5109 | 2768 | -0.01855 | 508072 NWTXARK7 345 511544 NWTXARK765 765 1 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | -1464.2 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 1 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 3 | -1834.8 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 1 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 2 | -1834.8 | -2768
108.0026 | 2989.5109 | 2768 | -0.01855 | 508072 NWTXARK7 345 511544 NWTXARK765 765 2 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | -1464.2 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 2 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 3 | -1834.8 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 2 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 1 | -1834.8 | -2768
108.0026 | 2989.5109 | 2768 | -0.01855 | 508072 NWTXARK7 345 511544 NWTXARK765 765 3 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | -1464.2 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 3 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 1 | -1834.8 | -2768
144.176 | 3990.7919 | 2768 | -0.02622 | 508072 NWTXARK7 345 511544 NWTXARK765 765 3 | C:508072 NWTXARK7 345 511544 NWTXARK765 765 2 | -1834.8 | -2768
252.3693 | 1665.6372 | 660 | 0.01012 | 508072 NWTXARK7 345 B$1265 NWTXARK1 1.00 1 | C:3Wnd: OPEN B$1266 NWTXARK2 2 | 833.5 | 660
255.9995 | 2711.0342 | 1059 | 0.02112 | 508298 LYDIA 7 345 508359 WELSH 7 345 1 | C:337376 7SAREPT 345 508809 LONGWD 7 345 1 | 974.4 | 1059
269.6308 | 2855.39 | 1059 | 0.02348 | 508298 LYDIA 7 345 508359 WELSH 7 345 1 | C:337561 8ELDEHV 500 337562 7ELDEHV 345 1 | 924.7 | 1059
282.2395 | 2988.9159 | 1059 | 0.02659 | 508298 LYDIA 7 345 508359 WELSH 7 345 1 | Base Case | 802.5 | 1059
438.3843 | 4642.4901 | 1059 | 0.03978 | 508298 LYDIA 7 345 508359 WELSH 7 345 1 | C:508072 NWTXARK7 345 508359 WELSH 7 345 1 | 1371.5 | 1059
115.4476 | 1357.6643 | 1176 | -0.01579 | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | C:511543 L.E.S.765 765 511544 NWTXARK765 765 2 | 59.3 | -1176
123.9004 | 1457.0691 | 1176 | -0.01678 | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | C:508072 NWTXARK7 345 508359 WELSH 7 345 1 | -77.3 | -1176
165.6268 | 1947.771 | 1176 | -0.01952 | 508298 LYDIA 7 345 510911 VALIANT7 345 1 | C:508072 NWTXARK7 345 508298 LYDIA 7 345 1 | -342.7 | -1176
177.6368 | 1881.174 | 1059 | 0.01548 | 508359 WELSH 7 345 508832 DIANA 7 345 1 | Base Case | 608.3 | 1059
217.6138 | 2304.5299 | 1059 | 0.02022 | 508359 WELSH 7 345 508832 DIANA 7 345 1 | C:508809 LONGWD 7 345 508841 WILKES 7 345 1 | 641.9 | 1059
237.628 | 2516.4801 | 1059 | 0.02141 | 508359 WELSH 7 345 508832 DIANA 7 345 1 | C:508359 WELSH 7 345 508841 WILKES 7 345 1 | 756 | 1059
299.9824 | 3176.8138 | 1059 | 0.02614 | 508359 WELSH 7 345 508832 DIANA 7 345 1 | C:508359 WELSH 7 345 508832 DIANA 7 345 2 | 1027.4 | 1059
174.8762 | 1851.9395 | 1059 | 0.01524 | 508359 WELSH 7 345 508832 DIANA 7 345 2 | Base Case | 598.8 | 1059
214.2719 | 2269.1396 | 1059 | 0.01991 | 508359 WELSH 7 345 508832 DIANA 7 345 2 | C:508809 LONGWD 7 345 508841 WILKES 7 345 1 | 632 | 1059
233.9514 | 2477.5452 | 1059 | 0.02108 | 508359 WELSH 7 345 508832 DIANA 7 345 2 | C:508359 WELSH 7 345 508841 WILKES 7 345 1 | 744.2 | 1059
298.588 | 3162.0465 | 1059 | 0.02602 | 508359 WELSH 7 345 508832 DIANA 7 345 2 | C:508359 WELSH 7 345 508832 DIANA 7 345 1 | 1022.5 | 1059
175.066 | 1853.9494 | 1059 | 0.01731 | 508359 WELSH 7 345 508841 WILKES 7 345 1 | Base Case | 430.6 | 1059
207.9925 | 2202.6409 | 1059 | 0.02018 | 508359 WELSH 7 345 508841 WILKES 7 345 1 | C:508359 WELSH 7 345 508832 DIANA 7 345 2 | 543.3 | 1059
208.9064 | 2212.319 | 1059 | 0.02026 | 508359 WELSH 7 345 508841 WILKES 7 345 1 | C:508359 WELSH 7 345 508832 DIANA 7 345 1 | 546.4 | 1059
217.9295 | 2307.873 | 1059 | 0.02226 | 508359 WELSH 7 345 508841 WILKES 7 345 1 | C:507760 SW SHV 7 345 508832 DIANA 7 345 1 | 477.5 | 1059
132.1471 | 1579.1579 | 1195 | -0.01444 | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | Base Case | -391.8 | -1195
151.0834 | 1805.4464 | 1195 | -0.01668 | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | -433.9 | -1195
160.3894 | 1916.6532 | 1195 | -0.01812 | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | C:507760 SW SHV 7 345 508832 DIANA 7 345 1 | -426.7 | -1195
160.656 | 1919.8397 | 1195 | -0.01762 | 508563 PIRKEY 7 345 508832 DIANA 7 345 1 | C:508359 WELSH 7 345 508841 WILKES 7 345 1 | -471 | -1195
108.1885 | 1292.8527 | 1195 | 0.01336 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | C:334028 7GRIMES 345 334029 7FRONTR 345 1 | 194.3 | 1195
113.3302 | 1354.2954 | 1195 | 0.01531 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | 95.4 | 1195
121.935 | 1457.1232 | 1195 | 0.01649 | 508572 LEBROCK7 345 508585 TENRUSK7 345 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | 101.2 | 1195
144.5821 | 1140.7527 | 789 | 0.01336 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Base Case | 42.2 | 789
163.847 | 1292.7527 | 789 | 0.01336 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | C:334028 7GRIMES 345 334029 7FRONTR 345 1 | 194.2 | 789
171.6344 | 1354.1954 | 789 | 0.01531 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | C:337368 8MTOLIV 500 337561 8ELDEHV 500 1 | 95.3 | 789
184.6671 | 1457.0232 | 789 | 0.01649 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | C:334325 8HARTBRG 500 337368 8MTOLIV 500 1 | 101.1 | 789
168.4299 | 1827.4644 | 1085 | -0.02046 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | Base Case | -145.1 | -1085
187.3666 | 2032.928 | 1085 | -0.02215 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | C:508359 WELSH 7 345 508832 DIANA 7 345 2 | -211.6 | -1085
187.9115 | 2038.8394 | 1085 | -0.0222 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | C:508359 WELSH 7 345 508832 DIANA 7 345 1 | -213.4 | -1085
219.6461 | 2383.16 | 1085 | -0.02652 | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | C:507760 SW SHV 7 345 508832 DIANA 7 345 1 | -202.5 | -1085
193.6859 | 954.8717 | 493 | -0.01036 | 508841 WILKES 7 345 B$1742 WILKES 1.00 1 | C:508359 WELSH 7 345 508841 WILKES 7 345 1 | 103 | -493
100.4197 | 1059.4276 | 1055 | 0.01043 | 509852 T.NO.--7 345 512650 GRDA1 7 345 1 | Base Case | 201.8 | 1055
114.0154 | 1202.8629 | 1055 | 0.01085 | 509852 T.NO.--7 345 512650 GRDA1 7 345 1 | C:3Wnd: OPEN B$1664 TULSA N 1 | 310.7 | 1055
126.7143 | 1336.8358 | 1055 | 0.01214 | 509852 T.NO.--7 345 512650 GRDA1 7 345 1 | C:506945 CHAMSPR7 345 509745 CLARKSV7 345 1 | 338.6 | 1055
135.0848 | 1425.1448 | 1055 | 0.01403 | 509852 T.NO.--7 345 512650 GRDA1 7 345 1 | C:300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 271.5 | 1055
148.8855 | 2405.9893 | 1616 | -0.01405 | 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | Base Case | -1250.7 | -1616
164.7613 | 2662.5425 | 1616 | -0.01587 | 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | C:532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | -1357.6 | -1616
164.9841 | 2666.1425 | 1616 | -0.01587 | 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | C:532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | -1361.2 | -1616
170.2555 | 2751.3294 | 1616 | -0.01546 | 509852 T.NO.--7 345 512694 CLEVLND7 345 1 | C:3Wnd: OPEN B$0582 CLVAUTO1 1 | -1480.1 | -1616
135.6814 | 3755.6604 | 2768 | -0.01031 | 511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | C:511543 L.E.S.765 765 514804 SOONER765 765 1 | -2907.9 | -2768
137.1779 | 3797.0844 | 2768 | -0.01068 | 511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | C:512694 CLEVLND7 345 514803 SOONER 7 345 1 | -2918.9 | -2768
164.7696 | 4560.8214 | 2768 | -0.01146 | 511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | C:525832 TUCO_INT 7 345 525833 TUCO765 765 1 | -3618.5 | -2768
228.7199 | 1639.9214 | 717 | 0.01146 | 511468 L.E.S.-7 345 515136 SUNNYSD7 345 1 | C:511543 L.E.S.765 765 511544 NWTXARK765 765 1 | 697.6 | 717
228.7199 | 1639.9214 | 717 | 0.01146 | 511468 L.E.S.-7 345 515136 SUNNYSD7 345 1 | C:511543 L.E.S.765 765 511544 NWTXARK765 765 2 | 697.6 | 717
146.4835 | 6694.2969 | 4570 | 0.07144 | 511543 L.E.S.765 765 511544 NWTXARK765 765 1 | C:511543 L.E.S.765 765 511544 NWTXARK765 765 2 | 820 | 4570
146.4835 | 6694.2969 | 4570 | 0.07144 | 511543 L.E.S.765 765 511544 NWTXARK765 765 2 | C:511543 L.E.S.765 765 511544 NWTXARK765 765 1 | 820 | 4570
117.396 | 5364.9988 | 4570 | -0.06255 | 511543 L.E.S.765 765 523080 KELTON765 765 1 | Base Case | 221.7 | -4570
136.4573 | 6236.0989 | 4570 | -0.07418 | 511543 L.E.S.765 765 523080 KELTON765 765 1 | C:514804 SOONER765 765 523080 KELTON765 765 1 | 136.5 | -4570
136.4573 | 6236.0989 | 4570 | -0.07418 | 511543 L.E.S.765 765 523080 KELTON765 765 1 | C:514804 SOONER765 765 523080 KELTON765 765 2 | 136.5 | -4570
155.4955 | 7106.1425 | 4570 | -0.08098 | 511543 L.E.S.765 765 523080 KELTON765 765 1 | C:511543 L.E.S.765 765 525833 TUCO765 765 1 | 447.4 | -4570
153.4532 | 1833.7655 | 1195 | 0.01139 | 512650 GRDA1 7 345 512750 TONECE7 345 1 | C:300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | 897.2 | 1195
252.6965 | 3019.7232 | 1195 | -0.01649 | 512694 CLEVLND7 345 514803 SOONER 7 345 1 | Base Case | -1663.8 | -1195
256.8924 | 3069.8648 | 1195 | -0.01588 | 512694 CLEVLND7 345 514803 SOONER 7 345 1 | C:300740 7SPORTSMAN 345 512650 GRDA1 7 345 1 | -1764.1 | -1195
259.3676 | 3099.4425 | 1195 | -0.01587 | 512694 CLEVLND7 345 514803 SOONER 7 345 1 | C:515224 MUSKOGE7 345 515302 FTSMITH7 345 1 | -1794.5 | -1195
266.0635 | 3179.4586 | 1195 | -0.01691 | 512694 CLEVLND7 345 514803 SOONER 7 345 1 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | -1789 | -1195
100.304 | 2776.4158 | 2768 | -0.01029 | 514803 SOONER 7 345 514804 SOONER765 765 1 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | -1930.3 | -2768
114.8589 | 3179.2944 | 2768 | -0.01046 | 514803 SOONER 7 345 514804 SOONER765 765 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -2319.2 | -2768
161.5136 | 4470.6977 | 2768 | -0.01347 | 514803 SOONER 7 345 514804 SOONER765 765 1 | C:514803 SOONER 7 345 514804 SOONER765 765 2 | -3363.1 | -2768
100.304 | 2776.4158 | 2768 | -0.01029 | 514803 SOONER 7 345 514804 SOONER765 765 2 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | -1930.3 | -2768
114.8589 | 3179.2944 | 2768 | -0.01046 | 514803 SOONER 7 345 514804 SOONER765 765 2 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -2319.2 | -2768
161.5136 | 4470.6977 | 2768 | -0.01347 | 514803 SOONER 7 345 514804 SOONER765 765 2 | C:514803 SOONER 7 345 514804 SOONER765 765 1 | -3363.1 | -2768
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 1 | C:514804 SOONER765 765 515304 FTSMITH765 765 2 | 1061.4 | 4570
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 1 | C:514804 SOONER765 765 515304 FTSMITH765 765 3 | 1061.4 | 4570
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 2 | C:514804 SOONER765 765 515304 FTSMITH765 765 1 | 1061.4 | 4570
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 2 | C:514804 SOONER765 765 515304 FTSMITH765 765 3 | 1061.4 | 4570
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 3 | C:514804 SOONER765 765 515304 FTSMITH765 765 2 | 1061.4 | 4570
125.5503 | 5737.6495 | 4570 | 0.05687 | 514804 SOONER765 765 515304 FTSMITH765 765 3 | C:514804 SOONER765 765 515304 FTSMITH765 765 1 | 1061.4 | 4570
105.4719 | 4820.0662 | 4570 | -0.05571 | 514804 SOONER765 765 523080 KELTON765 765 1 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | -239.2 | -4570
107.404 | 4908.3619 | 4570 | -0.05481 | 514804 SOONER765 765 523080 KELTON765 765 1 | C:514804 SOONER765 765 523080 KELTON765 765 2 | -401.5 | -4570
105.4719 | 4820.0662 | 4570 | -0.05571 | 514804 SOONER765 765 523080 KELTON765 765 2 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | -239.2 | -4570
107.404 | 4908.3619 | 4570 | -0.05481 | 514804 SOONER765 765 523080 KELTON765 765 2 | C:514804 SOONER765 765 523080 KELTON765 765 1 | -401.5 | -4570
121.726 | 5562.8787 | 4570 | -0.06299 | 514804 SOONER765 765 765343 MEDLDG765 765 1 | C:530610 POSTROCK765 765 532795 ROSEHIL765 765 1 | 383.4 | -4570
149.4037 | 6827.7471 | 4570 | -0.0773 | 514804 SOONER765 765 765343 MEDLDG765 765 1 | C:514804 SOONER765 765 765343 MEDLDG765 765 2 | 471.6 | -4570
121.726 | 5562.8787 | 4570 | -0.06299 | 514804 SOONER765 765 765343 MEDLDG765 765 2 | C:530610 POSTROCK765 765 532795 ROSEHIL765 765 1 | 383.4 | -4570
149.4037 | 6827.7471 | 4570 | -0.0773 | 514804 SOONER765 765 765343 MEDLDG765 765 2 | C:514804 SOONER765 765 765343 MEDLDG765 765 1 | 471.6 | -4570
101.996 | 1218.8525 | 1195 | -0.01098 | 514880 NORTWST7 345 515407 TATONGA7 345 1 | C:523080 KELTON765 765 523098 HITCHLAND765 765 1 | -316 | -1195
104.8507 | 1252.9655 | 1195 | -0.01139 | 514880 NORTWST7 345 515407 TATONGA7 345 1 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | -316.4 | -1195
113.8181 | 1360.1267 | 1195 | -0.01025 | 514880 NORTWST7 345 515407 TATONGA7 345 1 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | -517.3 | -1195
111.9269 | 3098.1357 | 2768 | 0.03073 | 515304 FTSMITH765 765 515305 FTSMITH8 500 1 | Base Case | 571.3 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 1 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 4 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 1 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 3 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 1 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 2 | 752.7 | 2768
111.9269 | 3098.1357 | 2768 | 0.03073 | 515304 FTSMITH765 765 515305 FTSMITH8 500 2 | Base Case | 571.3 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 2 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 4 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 2 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 1 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 2 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 3 | 752.7 | 2768
111.9269 | 3098.1357 | 2768 | 0.03073 | 515304 FTSMITH765 765 515305 FTSMITH8 500 3 | Base Case | 571.3 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 3 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 1 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 3 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 2 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 3 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 4 | 752.7 | 2768
111.9269 | 3098.1357 | 2768 | 0.03073 | 515304 FTSMITH765 765 515305 FTSMITH8 500 4 | Base Case | 571.3 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 4 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 1 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 4 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 2 | 752.7 | 2768
147.4737 | 4082.0712 | 2768 | 0.04049 | 515304 FTSMITH765 765 515305 FTSMITH8 500 4 | C:515304 FTSMITH765 765 515305 FTSMITH8 500 3 | 752.7 | 2768
102.1132 | 1220.2525 | 1195 | 0.01098 | 515375 WWRDEHV7 345 515407 TATONGA7 345 1 | C:523080 KELTON765 765 523098 HITCHLAND765 765 1 | 317.4 | 1195
104.9678 | 1254.3655 | 1195 | 0.01139 | 515375 WWRDEHV7 345 515407 TATONGA7 345 1 | C:511543 L.E.S.765 765 523080 KELTON765 765 1 | 317.8 | 1195
113.9437 | 1361.6267 | 1195 | 0.01025 | 515375 WWRDEHV7 345 515407 TATONGA7 345 1 | C:511468 L.E.S.-7 345 511543 L.E.S.765 765 1 | 518.8 | 1195
110.6909 | 3063.9253 | 2768 | -0.01227 | 523097 HITCHLAND 7 345 523098 HITCHLAND765 765 1 | C:523961 POTTER_CO 7 345 523962 POTTER765 765 1 | -2055 | -2768
140.8054 | 3897.4938 | 2768 | -0.01266 | 525832 TUCO_INT 7 345 525833 TUCO765 765 1 | C:523080 KELTON765 765 526825 BRISCOE765 765 1 | -2856.5 | -2768
140.9729 | 3902.1292 | 2768 | -0.01308 | 525832 TUCO_INT 7 345 525833 TUCO765 765 1 | C:511543 L.E.S.765 765 525833 TUCO765 765 1 | -2826.6 | -2768
174.8498 | 1253.6728 | 717 | 0.01292 | 531451 MINGO 7 345 640325 REDWILO3 345 1 | C:531453 MINGO765 765 640186 GENTLMN765 765 1 | 191.3 | 717
102.8073 | 4698.2924 | 4570 | 0.04957 | 531455 HOLCOMB765 765 765343 MEDLDG765 765 1 | C:530610 POSTROCK765 765 531453 MINGO765 765 1 | 622.3 | 4570
103.1422 | 4713.597 | 4570 | 0.04589 | 531455 HOLCOMB765 765 765343 MEDLDG765 765 1 | C:523080 KELTON765 765 523098 HITCHLAND765 765 1 | 940.2 | 4570
160.9433 | 1731.7499 | 1076 | 0.01044 | 532765 HOYT 7 345 532772 STRANGR7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 873.3 | 1076
246.2888 | 2354.5206 | 956 | -0.01128 | 532768 EMPEC 7 345 532769 LANG 7 345 1 | C:532768 EMPEC 7 345 532796 WICHITA7 345 1 | -1427 | -956
293.9855 | 2810.5017 | 956 | -0.01199 | 532768 EMPEC 7 345 532769 LANG 7 345 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -1824.6 | -956
424.3795 | 4057.0682 | 956 | -0.0166 | 532768 EMPEC 7 345 532769 LANG 7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -2692.1 | -956
194.6832 | 1861.1713 | 956 | 0.01027 | 532768 EMPEC 7 345 532774 SWISVAL7 345 1 | Base Case | 1016.7 | 956
214.6334 | 2051.8953 | 956 | 0.01064 | 532768 EMPEC 7 345 532774 SWISVAL7 345 1 | C:532772 STRANGR7 345 542982 IATAN 7 345 1 | 1177 | 956
227.6105 | 2175.9563 | 956 | 0.01179 | 532768 EMPEC 7 345 532774 SWISVAL7 345 1 | C:532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | 1206.5 | 956
315.4851 | 3016.0378 | 956 | 0.01488 | 532768 EMPEC 7 345 532774 SWISVAL7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1792.5 | 956
111.9502 | 3098.7802 | 2768 | -0.01912 | 532769 LANG 7 345 532776 LANG765 765 1 | C:532776 LANG765 765 543003 IATAN765 765 1 | -1526.6 | -2768
112.4861 | 3113.6152 | 2768 | -0.01249 | 532769 LANG 7 345 532776 LANG765 765 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -2086.6 | -2768
160.7854 | 4450.5389 | 2768 | -0.01744 | 532769 LANG 7 345 532776 LANG765 765 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -3016.5 | -2768
171.4575 | 2048.9171 | 1195 | 0.01056 | 532772 STRANGR7 345 532775 87TH 7 345 1 | C:542980 NASHUA 7 345 542982 IATAN 7 345 1 | 1180.6 | 1195
173.6428 | 2075.0319 | 1195 | 0.01133 | 532772 STRANGR7 345 532775 87TH 7 345 1 | C:542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 1143.4 | 1195
184.5981 | 2205.9476 | 1195 | 0.01228 | 532772 STRANGR7 345 532775 87TH 7 345 1 | C:532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | 1196.2 | 1195
180.0887 | 1721.6484 | 956 | 0.01246 | 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | Base Case | 697.1 | 956
222.434 | 2126.4692 | 956 | 0.01449 | 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | C:532772 STRANGR7 345 532775 87TH 7 345 1 | 935 | 956
222.7524 | 2129.5133 | 956 | 0.01442 | 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | C:532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | 943.8 | 956
268.3819 | 2565.7311 | 956 | 0.01582 | 532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1264.9 | 956
153.7029 | 1836.7499 | 1195 | 0.01044 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | C:532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | 978.3 | 1195
156.658 | 1872.0634 | 1195 | 0.01094 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | C:542980 NASHUA 7 345 542982 IATAN 7 345 1 | 972.5 | 1195
182.6898 | 2183.1435 | 1195 | 0.01376 | 532775 87TH 7 345 542977 CRAIG 7 345 1 | C:532774 SWISVAL7 345 542965 W.GRDNR7 345 1 | 1051.7 | 1195
107.3275 | 4904.8687 | 4570 | -0.03299 | 532776 LANG765 765 532795 ROSEHIL765 765 1 | C:543003 IATAN765 765 640354 PAULINE765 765 1 | -2192.2 | -4570
111.0579 | 5075.3458 | 4570 | -0.03051 | 532776 LANG765 765 532795 ROSEHIL765 765 1 | C:531453 MINGO765 765 640186 GENTLMN765 765 1 | -2566.6 | -4570
117.6002 | 5374.3313 | 4570 | -0.02516 | 532776 LANG765 765 532795 ROSEHIL765 765 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -3305.5 | -4570
183.6201 | 1755.4077 | 956 | -0.01325 | 532791 BENTON 7 345 532796 WICHITA7 345 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -665.9 | -956
187.6306 | 1793.7489 | 956 | -0.01255 | 532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | Base Case | -761.8 | -956
211.42 | 2021.1754 | 956 | -0.01346 | 532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -914.4 | -956
212.6475 | 2032.9099 | 956 | -0.0137 | 532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | C:532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | -906.4 | -956
218.7844 | 2091.5789 | 956 | -0.01418 | 532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | C:512694 CLEVLND7 345 514803 SOONER 7 345 1 | -925.6 | -956
136.9992 | 3792.1367 | 2768 | -0.01699 | 532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | Base Case | -2395.1 | -2768
159.9167 | 4426.4929 | 2768 | -0.01944 | 532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | C:532769 LANG 7 345 532776 LANG765 765 1 | -2828 | -2768
165.3073 | 4575.7072 | 2768 | -0.02012 | 532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -2921.3 | -2768
192.0606 | 5316.2379 | 2768 | -0.02422 | 532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | C:532776 LANG765 765 532795 ROSEHIL765 765 1 | -3324.7 | -2768
185.0365 | 1768.9488 | 956 | 0.01255 | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | Base Case | 737 | 956
208.8259 | 1996.3754 | 956 | 0.01346 | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 889.6 | 956
210.0533 | 2008.1099 | 956 | 0.0137 | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | C:532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | 881.6 | 956
216.2007 | 2066.8789 | 956 | 0.01418 | 532794 ROSEHIL7 345 532800 LATHAMS7 345 1 | C:512694 CLEVLND7 345 514803 SOONER 7 345 1 | 900.9 | 956
116.59 | 1259.1721 | 1080 | -0.01045 | 532796 WICHITA7 345 765342 MED-LDG5 345 1 | C:514804 SOONER765 765 765343 MEDLDG765 765 2 | -399.9 | -1080
120.7004 | 1303.5638 | 1080 | -0.01103 | 532796 WICHITA7 345 765342 MED-LDG5 345 1 | C:530610 POSTROCK765 765 532795 ROSEHIL765 765 1 | -396.6 | -1080
131.0901 | 1415.773 | 1080 | -0.01063 | 532796 WICHITA7 345 765342 MED-LDG5 345 1 | C:532796 WICHITA7 345 765342 MED-LDG5 345 2 | -541.7 | -1080
116.59 | 1259.1721 | 1080 | -0.01045 | 532796 WICHITA7 345 765342 MED-LDG5 345 2 | C:514804 SOONER765 765 765343 MEDLDG765 765 2 | -399.9 | -1080
120.7004 | 1303.5638 | 1080 | -0.01103 | 532796 WICHITA7 345 765342 MED-LDG5 345 2 | C:530610 POSTROCK765 765 532795 ROSEHIL765 765 1 | -396.6 | -1080
131.0901 | 1415.773 | 1080 | -0.01063 | 532796 WICHITA7 345 765342 MED-LDG5 345 2 | C:532796 WICHITA7 345 765342 MED-LDG5 345 1 | -541.7 | -1080
175.7402 | 2100.0953 | 1195 | 0.01064 | 532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | C:532793 NEOSHO 7 345 532800 LATHAMS7 345 1 | 1225.2 | 1195
188.2554 | 2249.6516 | 1195 | 0.0108 | 532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | C:532776 LANG765 765 532795 ROSEHIL765 765 1 | 1361.6 | 1195
195.7059 | 2338.6852 | 1195 | 0.01086 | 532797 WOLFCRK7 345 542981 LACYGNE7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 1445.7 | 1195
131.7742 | 950.0923 | 721 | 0.01001 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | Base Case | 127 | 721
176.0916 | 1269.6206 | 721 | 0.01128 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | 342.1 | 721
185.7212 | 1339.0501 | 721 | 0.01282 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | C:542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 284.9 | 721
186.8029 | 1346.8487 | 721 | 0.01484 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | C:541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | 126.6 | 721
114.3516 | 1299.0336 | 1136 | -0.01169 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | Base Case | -337.8 | -1136
136.8297 | 1554.385 | 1136 | -0.01315 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | C:542980 NASHUA 7 345 542982 IATAN 7 345 1 | -473.1 | -1136
145.8643 | 1657.0182 | 1136 | -0.01312 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | C:542982 IATAN 7 345 543003 IATAN765 765 1 | -578.2 | -1136
148.314 | 1684.847 | 1136 | -0.01448 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | C:542972 HAWTH 7 345 542980 NASHUA 7 345 1 | -494.2 | -1136
147.6732 | 1677.5681 | 1136 | 0.01193 | 541199 ST JOE 3 345 542980 NASHUA 7 345 1 | C:542980 NASHUA 7 345 542982 IATAN 7 345 1 | 696.6 | 1136
120.8622 | 871.4167 | 721 | 0.01047 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | C:542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 10.5 | 721
179.0722 | 1291.1103 | 721 | 0.01379 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | C:541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | -157.2 | 721
170.3227 | 1228.0268 | 721 | -0.01492 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | Base Case | 1.2 | -721
213.7908 | 1541.4314 | 721 | -0.0182 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | C:541197 SMARYVL7 345 645458 S3458 3 345 1 | -44.9 | -721
215.2946 | 1552.2742 | 721 | -0.01786 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | C:541198 PECULR 7 345 542968 STILWEL7 345 1 | -83.7 | -721
216.2058 | 1558.8436 | 721 | -0.01843 | 541201 SIBLEY 7 345 542972 HAWTH 7 345 1 | C:541198 PECULR 7 345 541200 PHILL 7 345 1 | -43.4 | -721
122.1859 | 1214.528 | 994 | 0.01052 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | Base Case | 349.5 | 994
142.3005 | 1414.4668 | 994 | 0.01166 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | C:542980 NASHUA 7 345 542982 IATAN 7 345 1 | 455.7 | 994
149.7824 | 1488.8375 | 994 | 0.0125 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | C:542972 HAWTH 7 345 542980 NASHUA 7 345 1 | 461 | 994
184.158 | 1830.5309 | 994 | 0.01344 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1 | C:542968 STILWEL7 345 542981 LACYGNE7 345 1 | 725.4 | 994
202.0463 | 2295.2459 | 1136 | -0.01659 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | Base Case | -931.1 | -1136
227.2617 | 2581.693 | 1136 | -0.01715 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | C:532772 STRANGR7 345 542982 IATAN 7 345 1 | -1171.5 | -1136
230.3656 | 2616.9537 | 1136 | -0.01821 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | C:532772 STRANGR7 345 532775 87TH 7 345 1 | -1119.6 | -1136
231.326 | 2627.8637 | 1136 | -0.01799 | 542972 HAWTH 7 345 542980 NASHUA 7 345 1 | C:3Wnd: OPEN B$1220 NASH 11 11 | -1148.6 | -1136
102.5093 | 2609.8879 | 2546 | -0.01607 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | C:541199 ST JOE 3 345 542980 NASHUA 7 345 1 | -1288.5 | -2546
105.7782 | 2693.112 | 2546 | -0.01415 | 542980 NASHUA 7 345 542982 IATAN 7 345 1 | C:541199 ST JOE 3 345 542982 IATAN 7 345 1 | -1529.6 | -2546
200.0835 | 5538.3121 | 2768 | -0.01882 | 542982 IATAN 7 345 543003 IATAN765 765 1 | C:640186 GENTLMN765 765 640444 HOOKER765 765 1 | -3990.8 | -2768
200.4899 | 5549.5612 | 2768 | -0.02212 | 542982 IATAN 7 345 543003 IATAN765 765 1 | Base Case | -3730.7 | -2768
226.1668 | 6260.2977 | 2768 | -0.0251 | 542982 IATAN 7 345 543003 IATAN765 765 1 | C:532768 EMPEC 7 345 532769 LANG 7 345 1 | -4196.4 | -2768
232.9729 | 6448.6889 | 2768 | -0.02559 | 542982 IATAN 7 345 543003 IATAN765 765 1 | C:532769 LANG 7 345 532776 LANG765 765 1 | -4344.5 | -2768
108.3308 | 1224.1384 | 1130 | 0.01268 | 547481 MON383 7 345 549984 BROOKLINE 7 345 1 | C:300045 7MORGAN 345 300739 7BLACKBERRY 345 1 | 181.5 | 1130
148.2809 | 1417.5654 | 956 | -0.01368 | 640277 MOORE 3 345 640312 PAULINE3 345 1 | C:543003 IATAN765 765 640354 PAULINE765 765 1 | -292.7 | -956
109.3502 | 3026.8128 | 2768 | -0.02129 | 765342 MED-LDG5 345 765343 MEDLDG765 765 1 | C:514804 SOONER765 765 765343 MEDLDG765 765 1 | -1276.2 | -2768
109.3502 | 3026.8128 | 2768 | -0.02129 | 765342 MED-LDG5 345 765343 MEDLDG765 765 1 | C:514804 SOONER765 765 765343 MEDLDG765 765 2 | -1276.2 | -2768
110.4692 | 3057.7866 | 2768 | -0.0158 | 765342 MED-LDG5 345 765343 MEDLDG765 765 1 | C:532794 ROSEHIL7 345 532795 ROSEHIL765 765 1 | -1758.6 | -2768
MISO_WUMS
185.943 | 1089.6259 | 586 | 0.01007 | 693580 CYPRESS 345 699247 ARCADN3 345 1 | C:693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | 261.6 | 586
201.8615 | 1182.9084 | 586 | 0.01105 | 693580 CYPRESS 345 699247 ARCADN3 345 1 | C:698870 GRANVL2 345 699329 GRANVL1 345 Z | 274.3 | 586
210.3756 | 1232.8009 | 586 | 0.01181 | 693580 CYPRESS 345 699247 ARCADN3 345 1 | C:699253 ARCADN1 345 699329 GRANVL1 345 1 | 261.7 | 586
195.9274 | 956.1259 | 488 | -0.01007 | 693580 CYPRESS 345 699304 FORST JT 345 1 | C:693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | -128.1 | -488
215.0427 | 1049.4084 | 488 | -0.01105 | 693580 CYPRESS 345 699304 FORST JT 345 1 | C:698870 GRANVL2 345 699329 GRANVL1 345 Z | -140.8 | -488
225.2666 | 1099.3009 | 488 | -0.01181 | 693580 CYPRESS 345 699304 FORST JT 345 1 | C:699253 ARCADN1 345 699329 GRANVL1 345 1 | -128.2 | -488
108.2873 | 1186.8289 | 1096 | 0.0107 | 693607 BARNHART 345 345 698870 GRANVL2 345 1 | C:693580 CYPRESS 345 699247 ARCADN3 345 1 | 307 | 1096
121.979 | 1336.8904 | 1096 | 0.01194 | 693607 BARNHART 345 345 698870 GRANVL2 345 1 | C:698871 GRANVL3 345 699396 CEDRSAUK 345 1 | 355.1 | 1096
131.9917 | 1446.6287 | 1096 | 0.01299 | 693607 BARNHART 345 345 698870 GRANVL2 345 1 | C:693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | 378.5 | 1096
120.8351 | 1160.0167 | 960 | 0.01047 | 693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | Base Case | 299.1 | 960
146.1095 | 1402.6514 | 960 | 0.01309 | 693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | C:693580 CYPRESS 345 699304 FORST JT 345 1 | 326.3 | 960
150.2345 | 1442.2514 | 960 | 0.01309 | 693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | C:693580 CYPRESS 345 699247 ARCADN3 345 1 | 365.9 | 960
174.3501 | 1673.7609 | 960 | 0.01507 | 693607 BARNHART 345 345 699396 CEDRSAUK 345 1 | C:693607 BARNHART 345 345 698870 GRANVL2 345 1 | 434.6 | 960
108.4711 | 1270.197 | 1171 | -0.011 | 698853 RACINE2 345 699367 ELM ROAD 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | -365.7 | -1171
117.1311 | 1371.6052 | 1171 | -0.01271 | 698853 RACINE2 345 699367 ELM ROAD 345 1 | C:270942 ZION ;0B 345 699247 ARCADN3 345 1 | -326.5 | -1171
119.845 | 1403.3855 | 1171 | -0.01324 | 698853 RACINE2 345 699367 ELM ROAD 345 1 | C:699253 ARCADN1 345 699432 PLS PR1 345 1 | -314.7 | -1171
101.9719 | 1441.8827 | 1414 | 0.01499 | 698853 RACINE2 345 699471 RACINE1 345 Z | C:699253 ARCADN1 345 699432 PLS PR1 345 1 | 209.3 | 1414
115.9896 | 1386.0758 | 1195 | -0.01355 | 698870 GRANVL2 345 698871 GRANVL3 345 Z | C:693607 BARNHART 345 345 698870 GRANVL2 345 1 | -271.9 | -1195
146.4316 | 1749.8581 | 1195 | 0.01682 | 698870 GRANVL2 345 699329 GRANVL1 345 Z | Base Case | 366.8 | 1195
164.079 | 1960.744 | 1195 | 0.01852 | 698870 GRANVL2 345 699329 GRANVL1 345 Z | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | 437.9 | 1195
182.2466 | 2177.8469 | 1195 | 0.02144 | 698870 GRANVL2 345 699329 GRANVL1 345 Z | C:693580 CYPRESS 345 699304 FORST JT 345 1 | 414.9 | 1195
188.1294 | 2248.1469 | 1195 | 0.02144 | 698870 GRANVL2 345 699329 GRANVL1 345 Z | C:693580 CYPRESS 345 699247 ARCADN3 345 1 | 485.2 | 1195
119.0756 | 1305.0685 | 1096 | -0.01202 | 698871 GRANVL3 345 699396 CEDRSAUK 345 1 | C:693580 CYPRESS 345 699304 FORST JT 345 1 | -316.7 | -1096
122.4606 | 1342.1685 | 1096 | -0.01202 | 698871 GRANVL3 345 699396 CEDRSAUK 345 1 | C:693580 CYPRESS 345 699247 ARCADN3 345 1 | -353.8 | -1096
143.0079 | 1567.3666 | 1096 | -0.01395 | 698871 GRANVL3 345 699396 CEDRSAUK 345 1 | C:693607 BARNHART 345 345 698870 GRANVL2 345 1 | -420.3 | -1096
285.1056 | 2600.1628 | 912 | 0.02477 | 698928 WERNER W 345 699359 N APPLETON 345 1 | Base Case | -563.4 | 912
298.6773 | 2723.9373 | 912 | 0.02642 | 698928 WERNER W 345 699359 N APPLETON 345 1 | C:270678 BYRON; B 345 274768 LEECO;BP 345 1 | -551.5 | 912
311.5216 | 2841.077 | 912 | 0.02774 | 698928 WERNER W 345 699359 N APPLETON 345 1 | C:699547 MORGAN 345 699602 HIWAY 22 345 1 | -560.1 | 912
322.8757 | 2944.6267 | 912 | 0.02884 | 698928 WERNER W 345 699359 N APPLETON 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -573.2 | 912
235.0633 | 1948.6745 | 829 | -0.02024 | 698928 WERNER W 345 699785 ROCKY RN 345 1 | Base Case | 284.4 | -829
267.6452 | 2218.7786 | 829 | -0.02343 | 698928 WERNER W 345 699785 ROCKY RN 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | 292.2 | -829
272.6217 | 2260.0336 | 829 | -0.02332 | 698928 WERNER W 345 699785 ROCKY RN 345 1 | C:698928 WERNER W 345 699602 HIWAY 22 345 1 | 342.5 | -829
318.6449 | 2641.5661 | 829 | -0.02778 | 698928 WERNER W 345 699785 ROCKY RN 345 1 | C:699602 HIWAY 22 345 699676 GARDR PK 345 1 | 357.3 | -829
139.3726 | 1866.1989 | 1339 | 0.0207 | 699244 ARP 345 345 699785 ROCKY RN 345 1 | Base Case | -164.1 | 1339
147.6994 | 1977.6949 | 1339 | 0.02218 | 699244 ARP 345 345 699785 ROCKY RN 345 1 | C:699449 ARROWHD 345 699450 ST LAKE 345 1 | -153.9 | 1339
160.1123 | 2143.9035 | 1339 | 0.02398 | 699244 ARP 345 345 699785 ROCKY RN 345 1 | C:636400 HILLS 3 345 700543 HILLS 3 765 765 N1 | -172.1 | 1339
172.6787 | 2312.1675 | 1339 | 0.02576 | 699244 ARP 345 345 699785 ROCKY RN 345 1 | C:699450 ST LAKE 345 699676 GARDR PK 345 1 | -194 | 1339
134.8791 | 1478.2748 | 1096 | -0.01566 | 699253 ARCADN1 345 699329 GRANVL1 345 1 | Base Case | -190.6 | -1096
154.1114 | 1689.0607 | 1096 | -0.01736 | 699253 ARCADN1 345 699329 GRANVL1 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | -261.6 | -1096
174.6023 | 1913.6417 | 1096 | -0.02036 | 699253 ARCADN1 345 699329 GRANVL1 345 1 | C:693580 CYPRESS 345 699304 FORST JT 345 1 | -239.5 | -1096
181.1169 | 1985.0417 | 1096 | -0.02036 | 699253 ARCADN1 345 699329 GRANVL1 345 1 | C:693580 CYPRESS 345 699247 ARCADN3 345 1 | -310.9 | -1096
125.4704 | 1094.1022 | 872 | 0.01208 | 699253 ARCADN1 345 699432 PLS PR1 345 1 | C:698853 RACINE2 345 699367 ELM ROAD 345 1 | 100.8 | 872
133.0858 | 1160.5086 | 872 | 0.01343 | 699253 ARCADN1 345 699432 PLS PR1 345 1 | C:270942 ZION ;0B 345 699247 ARCADN3 345 1 | 56.2 | 872
144.9647 | 1264.0919 | 872 | 0.01459 | 699253 ARCADN1 345 699432 PLS PR1 345 1 | C:699432 PLS PR1 345 699471 RACINE1 345 1 | 64.4 | 872
104.5565 | 1145.9396 | 1096 | -0.01295 | 699304 FORST JT 345 699556 FOXRIVER 345 1 | C:699359 N APPLETON 345 699669 FTZGERLD 345 1 | -81.1 | -1096
110.357 | 1209.5127 | 1096 | -0.01195 | 699304 FORST JT 345 699556 FOXRIVER 345 1 | C:698900 PT BCH4 345 699211 PT BCH3 345 Z | -226.9 | -1096
128.9705 | 1413.5172 | 1096 | -0.01523 | 699304 FORST JT 345 699556 FOXRIVER 345 1 | C:698898 PT BCH2 345 699211 PT BCH3 345 Z | -161.2 | -1096
101.1033 | 1108.0925 | 1096 | -0.01239 | 699432 PLS PR1 345 699471 RACINE1 345 1 | Base Case | -89.3 | -1096
122.8621 | 1346.5684 | 1096 | -0.01431 | 699432 PLS PR1 345 699471 RACINE1 345 1 | C:270695 CHERR; R 345 270883 SILVE; R 345 1 | -169.9 | -1096
132.6267 | 1453.5887 | 1096 | -0.01625 | 699432 PLS PR1 345 699471 RACINE1 345 1 | C:270942 ZION ;0B 345 699247 ARCADN3 345 1 | -117.4 | -1096
136.2827 | 1493.6586 | 1096 | -0.01691 | 699432 PLS PR1 345 699471 RACINE1 345 1 | C:699253 ARCADN1 345 699432 PLS PR1 345 1 | -103.2 | -1096
130.6735 | 1426.9547 | 1092 | 0.0161 | 699450 ST LAKE 345 699676 GARDR PK 345 1 | C:699244 ARP 345 345 699785 ROCKY RN 345 1 | -103.1 | 1092
141.5381 | 1545.5961 | 1092 | 0.01778 | 699450 ST LAKE 345 699676 GARDR PK 345 1 | C:601028 EAU CL 3 345 699244 ARP 345 345 1 | -83.6 | 1092
Note on A2: JMB: Estimated Percent Loading in Final Case
Note on B2: JMB: Estimated Loading in Final Case
Note on D2: PTI: Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on G2: PTI: MW Flow before the transfer
Note on H2: PTI: Rating (Base case or Contingent)